## Sheet1
TAG_NUMBER | TAG_NUMBER.1 | TYPE_OF_INST | DESCRIPTION | MEDIUM | QTY/BOILER | LINE_SIZE | OP_PRESS | MAX_PRESS | UNIT_OF_PRESS | OP_TEMP | MAX_TEMP | UNIT_OF_TEMP | OP_OTHERS | MAX_OTHERS | UNIT_OF_OTHERS | MAX_VELOCITY (m/sec) | INSULATION_THICKNESS (mm) | FUNCTION | SET POINT | UNIT | RANGE_OF_PY_INST | UNIT_OF_PY_INST | RANGE _OF_SEC_INST | UNIT_OF_SEC_INST | CONTACT ACTION | INST_END_CONN | SCOPE | REVISION | REMARKS | TYPE OF PROTOCOL (HART/PROFIBUS) | LINE_ITEM | Unit
60HAC10CT001 | 60HAC10CT001 | TYPE-K TC | ECON INLET BOILER FW TEMP | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | 10 | 150 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60LAB91CT001 | 60LAB91CT001 | TT | FEED WATER LINE DRAIN | METAL | 1 | -- |  |  | kg/cm² |  |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- |  | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC10CT002 | 60HAC10CT002 | TYPE-K TC | ECON INLET BOILER FW TEMP | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | 10 | 150 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAG15CT002 | 60HAG15CT002 | TT | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | -- | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC10CT003 | 60HAC10CT003 | TYPE-K TC | ECON DRAIN TEMP | METAL | 1 | 114.3x20 | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAG15CT003 | 60HAG15CT003 | TT | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | -- | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC20CT001 | 60HAC20CT001 | TYPE-K TC | ECON OUTLET LINK | WATER | 1 | 508x70 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 170 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE WITH EXTENSION LENGTH-30 MTS
60HAG15CT004 | 60HAG15CT004 | TT | WARM UP LINE TO BLR RECIRC SYS TEMP | WATER | 1 | -- | 309.7 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG15CP002 | 60HAG15CP002 | PDT | STARTUP SYSTEM MIXING PIECE | WATER | 1 | 508x70 | 313.8 | 353.5 | kg/cm² | 309 | 348 | °C | 0.2 to 0.5 | -- | kg/cm² | -- | -- | D/I | -- | -- | 0 to 5 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAC20CT002 | 60HAC20CT002 | TYPE-K TC | ECON OUTLET LINK | WATER | 1 | 508x70 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 170 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE WITH EXTENSION LENGTH-30 MTS
60HAG15CT005 | 60HAG15CT005 | TT | BWCP SUCTION LINE | WATER | 1 | -- | 315.2 | 353.5 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CP001 | 60HAG25CP001 | PDT | BOILER WATER CIRC PUMP | WATER | 1 | 508x70 / 406.4x55 | 171.42 | 352.7 | kg/cm² | 309 | 357 | °C |  | -- | kg/cm² | -- | -- | D/I,C,N | Min Head =120 | m | 0 to 25 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAG25CP002 | 60HAG25CP002 | PDT | BOILER WATER CIRC PUMP | WATER | 1 | 508x70 / 406.4x55 | 171.42 | 352.7 | kg/cm² | 309 | 357 | °C |  | -- | kg/cm² | -- | -- | D/I,C,N | Min Head =120 | m | 0 to 25 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAG25CP003 | 60HAG25CP003 | PDT | BOILER WATER CIRC PUMP | WATER | 1 | 508x70 / 406.4x55 | 171.42 | 352.7 | kg/cm² | 309 | 357 | °C |  | -- | kg/cm² | -- | -- | D/I,C,N | Min Head =120 | m | 0 to 25 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAG27CP501 | 60HAG27CP501 | PI | BWCP COOLING WTR SUPPLY PRESS | WATER | 1 | 88.9x5.49 | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HAG27CT001 | 60HAG27CT001 | PT-100 | BWCP COOLING WTR SUPPLY TEMP | WATER | 1 | 88.9x5.49 | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | 8 | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 0
60HAG27CT001 | 60HAG27CT001 | TT | BWCP COOLING WTR SUPPLY TEMP | WATER | 1 | -- | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG27CT501 | 60HAG27CT501 | TI | BWCP COOLING WTR SUPPLY TEMP | WATER | 1 | 88.9x5.49 | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60HAG27CT502 | 60HAG27CT502 | TI | BWCP COOLING WTR RETURN TEMP | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60HAG27CT002 | 60HAG27CT002 | PT-100 | BWCP COOLING WTR RETURN TEMP | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | 8 | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 0
60HAG27CT002 | 60HAG27CT002 | TT | BWCP COOLING WTR RETURN TEMP | WATER | 1 | -- | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG27CF101 | 60HAG27CF101 | FIS | BWCP COOLING WTR RETURN FLOW | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C |  | -- | m³/h | -- | -- | D/I,A,N | Low Alarm= | m³/h | -- | -- | -- | -- | COD | -- | V | 0
60HAG27CT503 | 60HAG27CT503 | TI | BWCP HEAT BARRIER COOLING WTR RETURN TEMP | WATER | 1 | 33.4x3.38 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60HAG27CF102 | 60HAG27CF102 | FIS | BWCP HEAT BARRIER COOLING WTR RETURN FLOW | WATER | 1 | 33.4x3.38 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C |  | -- | m³/h | -- | -- | D/I,A,N | Low Alarm= | m³/h | -- | -- | -- | -- | COD | -- | V | 0
60HAG27CP502 | 60HAG27CP502 | PI | BWCP COOLING WTR RETURN PRESS (COMMON LINE) | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HAG25CT001 | 60HAG25CT001 | TYPE-K TC | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 0
60HAG25CT001 | 60HAG25CT001 | TT | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | ** ΔT = 100 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB. ** PUMP CASING / PUMP WATER SUPPLY LINE ΔT | PROFIBUS
60HAG25CT005 | 60HAG25CT005 | TYPE-K TC | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 0
60HAG25CT005 | 60HAG25CT005 | TT | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | ** ΔT = 100 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB. ** PUMP CASING / PUMP WATER SUPPLY LINE ΔT | PROFIBUS
60HAG25CT002 | 60HAG25CT002 | TYPE-K TC | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 0
60HAG25CT003 | 60HAG25CT003 | TYPE-K TC | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 0
60HAG25CT004 | 60HAG25CT004 | TYPE-K TC | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 0
60HAG25CT002 | 60HAG25CT002 | TT | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | High Alarm= 63 , High Trip= 66 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CT003 | 60HAG25CT003 | TT | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | High Alarm= 63 , High Trip= 66 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CT004 | 60HAG25CT004 | TT | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | High Alarm= 63 , High Trip= 66 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CT501 | 60HAG25CT501 | TI | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | V | 0
60LCR25CP501 | 60LCR25CP501 | PI | BOILER RECIR PUMP MOTOR LP FILL WTR PRESS | WATER | 1 | 33.4x4.55 | 28.5 | 50 | kg/cm² | 27 | 55 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LCR25CT501 | 60LCR25CT501 | TI | BOILER RECIR PUMP MOTOR LP FILL WTR TEMP | WATER | 1 | 33.4x4.55 | 28.5 | 50 | kg/cm² | 27 | 55 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60LCR25CP101 | 60LCR25CP101 | PDIS | BOILER RECIR PUMP MOTOR LP FILL WTR LINE FILTER DIFF PRESS | WATER | 1 | 33.4x4.55 | 28.5 | 50 | kg/cm² | 27 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- |  | kg/cm² | -- | -- | -- | -- | V | 0
60HAC10CP501 | 60HAC10CP501 | PI | ECON INLET BOILER FW PRESS | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HAC10CP401 | 60HAC10CP401 | PP | ECON INLET BOILER FW PRESS | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAC10CF501 | 60HAC10CF501 | FE | ECON INLET BOILER FW FLOW | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60HAC10CF001 | 60HAC10CF001 | FT | ECON INLET BOILER FW FLOW | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | D/I,A,N | Low Alarm=864.35 Low Trip=800.47 | t/hr | Later | mmWC | 0 to 2600 | t/hr | -- | -- | P | 0 |  | HART
60HAC10CF002 | 60HAC10CF002 | FT | ECON INLET BOILER FW FLOW | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | D/I,A,N | Low Alarm=864.35 Low Trip=800.47 | t/hr | Later | mmWC | 0 to 2600 | t/hr | -- | -- | P | 0 |  | HART
60HAC10CF003 | 60HAC10CF003 | FT | ECON INLET BOILER FW FLOW | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | D/I,A,N | Low Alarm=864.35 Low Trip=800.47 | t/hr | Later | mmWC | 0 to 2600 | t/hr | -- | -- | P | 0 |  | HART
60HAC10CP001 | 60HAC10CP001 | PT | ECON INLET BOILER FW PRESS | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAC20CT003 | 60HAC20CT003 | TYPE-K TC | ECON MIXING LINE | WATER | 1 | 711x95 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAC10CT001 | 60HAC10CT001 | TT | ECON INLET BOILER FW TEMP | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAC20CT004 | 60HAC20CT004 | TYPE-K TC | ECON MIXING LINE | WATER | 1 | 711x95 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAC10CT002 | 60HAC10CT002 | TT | ECON INLET BOILER FW TEMP | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAC10CT401 | 60HAC10CT401 | TW | ECON INLET BOILER FW TEMP | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAD03CT001 | 60HAD03CT001 | TYPE-K TC | FURN LWR FRONT & REAR INLET HDR DRAIN TEMP | METAL | 1 | 114.3x20 | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAC10CT003 | 60HAC10CT003 | TT | ECON DRAIN TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC11CT001 to 006 | 60HAC11CT001 to 006 | TYPE-K TC | ECON INLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | T | 0
60HAC11CT001 to 006 | 60HAC11CT001 to 006 | TT | ECON INLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC12CT001 to 006 | 60HAC12CT001 to 006 | TYPE-K TC | ECON OUTLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | T | 0
60HAC12CT001 to 006 | 60HAC12CT001 to 006 | TT | ECON OUTLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD10CT132 | 60HAD10CT132 | TYPE-K TC | FURN INTER. LEFT SIDE HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0
60HAC20CT001 | 60HAC20CT001 | TT | ECON OUTLET LINK | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD20CT141 | 60HAD20CT141 | TYPE-K TC | FURN INTER. FRONT HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0
60HAC20CT002 | 60HAC20CT002 | TT | ECON OUTLET LINK | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD30CT141 | 60HAD30CT141 | TYPE-K TC | FURN INTER. REAR HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0
60HAC20CT003 | 60HAC20CT003 | TT | ECON MIXING LINE | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD40CT132 | 60HAD40CT132 | TYPE-K TC | FURN INTER.RIGHT SIDE HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0
60HAC20CT004 | 60HAC20CT004 | TT | ECON MIXING LINE | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD81CT009 | 60HAD81CT009 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | WATER | 1 |  | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | 250 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAD03CT001 | 60HAD03CT001 | TT | FURN LWR FRONT & REAR INLET HDR DRAIN TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD10CT001 to 019 | 60HAD10CT001 to 019 | TYPE-K TC | LEFT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0
60HAD10CT001 to 019 | 60HAD10CT001 to 019 | TT | LEFT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD10CT020 to 131 | 60HAD10CT020 to 131 | TYPE-K TC | LEFT SPIRAL WALL TUBE | METAL | 112 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAD15CT001 to 019 | 60HAD15CT001 to 019 | TYPE-K TC | LEFT VERT WALL OUTLET TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm (HA) = Refer remarks | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O. HA=511°C FOR TUBE 1. HA=524°C FOR TUBES 23, 45, 67. HA=512°C FOR TUBES 89, 111, 133, 155, 177. HA=524°C FOR TUBES 199, 221, 243, 265, 287, 309, 331, 353, 375, 393.
60HAD15CT020 to 393 | 60HAD15CT020 to 393 | TYPE-K TC | LEFT VERT WALL OUTLET TUBE | METAL | 374 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAD82CT009 | 60HAD82CT009 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | WATER | 1 |  | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | 250 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAD10CT132 | 60HAD10CT132 | TT | FURN INTER. LEFT SIDE HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD20CT001 to 020 | 60HAD20CT001 to 020 | TYPE-K TC | FRONT SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0
60HAD20CT001 to 020 | 60HAD20CT001 to 020 | TT | FRONT SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD20CT021 to 140 | 60HAD20CT021 to 140 | TYPE-K TC | FRONT SPIRAL WALL TUBE | METAL | 120 | -- | -- | -- | kg/cm² |  | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAD25CT001 to 020 | 60HAD25CT001 to 020 | TYPE-K TC | FRONT VERT WALL OUTLET TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm= 510 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAD25CT021 to 420 | 60HAD25CT021 to 420 | TYPE-K TC | FRONT VERT WALL OUTLET TUBE | METAL | 400 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAG15CT001 | 60HAG15CT001 | TYPE-K TC | WTR STORAGE TANK DOWNCOMER TEMP | WATER | 1 | 508x70 | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAD20CT141 | 60HAD20CT141 | TT | FURN INTER. FRONT HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD30CT001 to 020 | 60HAD30CT001 to 020 | TYPE-K TC | REAR SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0
60HAD30CT001 to 020 | 60HAD30CT001 to 020 | TT | REAR SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD30CT021 to 140 | 60HAD30CT021 to 140 | TYPE-K TC | REAR SPIRAL WALL TUBE | METAL | 120 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAD35CT001 to 020 | 60HAD35CT001 to 020 | TYPE-K TC | REAR VERT WALL HANGER TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm (HA) = Refer remarks | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O. HA=494°C FOR TUBES 1, 23, 45, 89, 111, 155, 177, 221, 243, 287, 309, 353, 375, 419. HA=496°C FOR TUBES 67, 133, 199, 265, 331, 397.
60HAD35CT021 to 420 | 60HAD35CT021 to 420 | TYPE-K TC | REAR VERT WALL HANGER TUBE | METAL | 400 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAG15CT002 | 60HAG15CT002 | TYPE-K TC | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | 508x70 | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAD30CT141 | 60HAD30CT141 | TT | FURN INTER. REAR HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD40CT001 to 019 | 60HAD40CT001 to 019 | TYPE-K TC | RIGHT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0
60HAD40CT001 to 019 | 60HAD40CT001 to 019 | TT | RIGHT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD40CT020 to 131 | 60HAD40CT020 to 131 | TYPE-K TC | RIGHT SPIRAL WALL TUBE | METAL | 112 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAD45CT001 to 019 | 60HAD45CT001 to 019 | TYPE-K TC | RIGHT VERT WALL PANEL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm (HA) = Refer remarks | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O. HA=511°C FOR TUBE 393. HA=524°C FOR TUBES 353, 375. HA=512°C FOR TUBES 243, 265, 287, 309, 331. HA=524°C FOR TUBES 1, 23, 45, 67, 89, 111, 133, 155, 177, 199, 221.
60HAD45CT020 to 393 | 60HAD45CT020 to 393 | TYPE-K TC | RIGHT VERT WALL PANEL TUBE | METAL | 374 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAG15CT003 | 60HAG15CT003 | TYPE-K TC | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | 508x70 | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAD40CT132 | 60HAD40CT132 | TT | FURN INTER.RIGHT SIDE HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH01CP001 | 60HAH01CP001 | PT | WATER SEPARATOR "A" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAG15CT004 | 60HAG15CT004 | TYPE-K TC | WARM UP LINE TO BLR RECIRC SYS TEMP | WATER | 1 | 508x70 | 309.7 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAH01CT001 | 60HAH01CT001 | TT | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH01CT401 | 60HAH01CT401 | TW | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH01CP002 | 60HAH01CP002 | PT | WATER SEPARATOR "A" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAG15CT005 | 60HAG15CT005 | TYPE-K TC | BWCP SUCTION LINE | WATER | 1 | 508x70 | 315.2 | 353.5 | kg/cm² | 309 | 348 | °C | -- | -- | -- | 5 | 150 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0
60HAH01CT002 | 60HAH01CT002 | TT | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH01CT402 | 60HAH01CT402 | TW | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH01CT001 | 60HAH01CT001 | TYPE-K TC | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH01CT003 | 60HAH01CT003 | TT | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH01CT002 | 60HAH01CT002 | TYPE-K TC | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH01CT004 | 60HAH01CT004 | TT | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH02CP001 | 60HAH02CP001 | PT | WATER SEPARATOR "B" OUTLET PRESS | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAH01CT003 | 60HAH01CT003 | TYPE-K TC | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAH02CT001 | 60HAH02CT001 | TT | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | -- | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH02CT401 | 60HAH02CT401 | TW | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH02CP002 | 60HAH02CP002 | PT | WATER SEPARATOR "B" OUTLET PRESS | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAH01CT004 | 60HAH01CT004 | TYPE-K TC | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAH02CT002 | 60HAH02CT002 | TT | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | -- | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH02CT402 | 60HAH02CT402 | TW | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH02CT001 | 60HAH02CT001 | TYPE-K TC | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | 30 | 240 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH02CT003 | 60HAH02CT003 | TT | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH02CT002 | 60HAH02CT002 | TYPE-K TC | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | 30 | --- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH02CT004 | 60HAH02CT004 | TT | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH03CP001 | 60HAH03CP001 | PT | WATER SEPARATOR "C" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAH02CT003 | 60HAH02CT003 | TYPE-K TC | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAH03CT001 | 60HAH03CT001 | TT | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH03CT401 | 60HAH03CT401 | TW | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH03CP002 | 60HAH03CP002 | PT | WATER SEPARATOR "C" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAH02CT004 | 60HAH02CT004 | TYPE-K TC | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAH03CT002 | 60HAH03CT002 | TT | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH03CT402 | 60HAH03CT402 | TW | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH03CT001 | 60HAH03CT001 | TYPE-K TC | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH03CT003 | 60HAH03CT003 | TT | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH03CT002 | 60HAH03CT002 | TYPE-K TC | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH03CT004 | 60HAH03CT004 | TT | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH04CP001 | 60HAH04CP001 | PT | WATER SEPARATOR "D" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAH03CT003 | 60HAH03CT003 | TYPE-K TC | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAH04CT001 | 60HAH04CT001 | TT | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH04CT401 | 60HAH04CT401 | TW | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH04CP002 | 60HAH04CP002 | PT | WATER SEPARATOR "D" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAH03CT004 | 60HAH03CT004 | TYPE-K TC | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAH04CT002 | 60HAH04CT002 | TT | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH04CT402 | 60HAH04CT402 | TW | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH04CT001 | 60HAH04CT001 | TYPE-K TC | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH04CT003 | 60HAH04CT003 | TT | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH04CT002 | 60HAH04CT002 | TYPE-K TC | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH04CT004 | 60HAH04CT004 | TT | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD71CT001 | 60HAD71CT001 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT002 | 60HAD71CT002 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT003 | 60HAD71CT003 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT004 | 60HAD71CT004 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT005 | 60HAD71CT005 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT006 | 60HAD71CT006 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT007 | 60HAD71CT007 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT008 | 60HAD71CT008 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD71CT001 | 60HAD71CT001 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT002 | 60HAD71CT002 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT003 | 60HAD71CT003 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT004 | 60HAD71CT004 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT005 | 60HAD71CT005 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT006 | 60HAD71CT006 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT007 | 60HAD71CT007 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT008 | 60HAD71CT008 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT001 | 60HAD72CT001 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT002 | 60HAD72CT002 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT003 | 60HAD72CT003 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT004 | 60HAD72CT004 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT005 | 60HAD72CT005 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT006 | 60HAD72CT006 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT007 | 60HAD72CT007 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT008 | 60HAD72CT008 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD72CT001 | 60HAD72CT001 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT002 | 60HAD72CT002 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT003 | 60HAD72CT003 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT004 | 60HAD72CT004 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT005 | 60HAD72CT005 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT006 | 60HAD72CT006 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT007 | 60HAD72CT007 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT008 | 60HAD72CT008 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT001 | 60HAD73CT001 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT002 | 60HAD73CT002 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT003 | 60HAD73CT003 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT004 | 60HAD73CT004 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT005 | 60HAD73CT005 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT006 | 60HAD73CT006 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT007 | 60HAD73CT007 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT008 | 60HAD73CT008 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD73CT001 | 60HAD73CT001 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT002 | 60HAD73CT002 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT003 | 60HAD73CT003 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT004 | 60HAD73CT004 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT005 | 60HAD73CT005 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT006 | 60HAD73CT006 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT007 | 60HAD73CT007 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT008 | 60HAD73CT008 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT001 | 60HAD74CT001 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT002 | 60HAD74CT002 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT003 | 60HAD74CT003 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT004 | 60HAD74CT004 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT005 | 60HAD74CT005 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT006 | 60HAD74CT006 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT007 | 60HAD74CT007 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT008 | 60HAD74CT008 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD74CT001 | 60HAD74CT001 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT002 | 60HAD74CT002 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT003 | 60HAD74CT003 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT004 | 60HAD74CT004 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT005 | 60HAD74CT005 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT006 | 60HAD74CT006 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT007 | 60HAD74CT007 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT008 | 60HAD74CT008 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CL001 | 60HAD81CL001 | LT | SEPARATOR STRG TANK "A" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 0 |  | HART
60HAD81CL002 | 60HAD81CL002 | LT | SEPARATOR STRG TANK "A" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 0 |  | HART
60HAD81CL003 | 60HAD81CL003 | LT | SEPARATOR STRG TANK "A" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 0 |  | HART
60HAD81CP001 | 60HAD81CP001 | PT | SEPARATOR STRG TANK "A" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAD81CP002 | 60HAD81CP002 | PT | SEPARATOR STRG TANK "A" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAD81CT001 | 60HAD81CT001 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD81CT002 | 60HAD81CT002 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD81CT003 | 60HAD81CT003 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD81CT004 | 60HAD81CT004 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD81CT005 | 60HAD81CT005 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD81CT006 | 60HAD81CT006 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD81CT007 | 60HAD81CT007 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD81CT008 | 60HAD81CT008 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAH04CT003 | 60HAH04CT003 | TYPE-K TC | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAD81CT001 | 60HAD81CT001 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT002 | 60HAD81CT002 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT003 | 60HAD81CT003 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT004 | 60HAD81CT004 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT005 | 60HAD81CT005 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT006 | 60HAD81CT006 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT007 | 60HAD81CT007 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT008 | 60HAD81CT008 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT009 | 60HAD81CT009 | TT | SEPARATOR STRG TANK "A" TEMP | WATER | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CL001 | 60HAD82CL001 | LT | SEPARATOR STRG TANK "B" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 0 |  | HART
60HAD82CL002 | 60HAD82CL002 | LT | SEPARATOR STRG TANK "B" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 0 |  | HART
60HAD82CL003 | 60HAD82CL003 | LT | SEPARATOR STRG TANK "B" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 0 |  | HART
60HAD82CP001 | 60HAD82CP001 | PT | SEPARATOR STRG TANK "B" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAD82CP002 | 60HAD82CP002 | PT | SEPARATOR STRG TANK "B" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | HART
60HAD82CT001 | 60HAD82CT001 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD82CT002 | 60HAD82CT002 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD82CT003 | 60HAD82CT003 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD82CT004 | 60HAD82CT004 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD82CT005 | 60HAD82CT005 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD82CT006 | 60HAD82CT006 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD82CT007 | 60HAD82CT007 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAD82CT008 | 60HAD82CT008 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 0
60HAH04CT004 | 60HAH04CT004 | TYPE-K TC | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAD82CT001 | 60HAD82CT001 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT002 | 60HAD82CT002 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT003 | 60HAD82CT003 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT004 | 60HAD82CT004 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT005 | 60HAD82CT005 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT006 | 60HAD82CT006 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT007 | 60HAD82CT007 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT008 | 60HAD82CT008 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT009 | 60HAD82CT009 | TT | SEPARATOR STRG TANK "B" TEMP | WATER | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAG11CL001 | 60HAG11CL001 | LT | SEPARATOR STRG TANK "A" DNCOMER LEVEL | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | DP=0.24 | -- | kg/cm² | -- | -- | D/I,C | High Alarm= 0.42 Low Alarm= 0.04 Control=$ | kg/cm² | 0 to 0.8 | kg/cm² | -- | -- | -- | -- | P | 0 | $ - Control set point is middle of F-49 Downcomer | HART
60HAG12CL001 | 60HAG12CL001 | LT | SEPARATOR STRG TANK "B" DNCOMER LEVEL | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | DP=0.24 | -- | kg/cm² | -- | -- | D/I,C | High Alarm= 0.42 Low Alarm= 0.04 Control=$ | kg/cm² | 0 to 0.8 | kg/cm² | -- | -- | -- | -- | P | 0 | $ - Control set point is middle of F-49 Downcomer | HART
60HAH05CT001 | 60HAH05CT001 | TYPE-K TC | SH FURN ROOF INLET HDR DRAIN TEMP | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAG15CT001 | 60HAG15CT001 | TT | WTR STORAGE TANK DOWNCOMER TEMP | WATER | 1 | -- | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG15CT401 | 60HAG15CT401 | TW | WTR STORAGE TANK DOWNCOMER TEMP | WATER | 1 | 508x70 | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAG15CP001 | 60HAG15CP001 | PT | WTR STORAGE TANK DOWNCOMER PRESS | WATER | 1 | 508x70 | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH14CT001 | 60HAH14CT001 | TYPE-K TC | BP LOWER FRONT HDR DRAIN TEMP | METAL | 1 | 88.9x20 | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH05CT001 | 60HAH05CT001 | TT | SH FURN ROOF INLET HDR DRAIN TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH14CT002 | 60HAH14CT002 | TYPE-K TC | BP LOWER REAR HDR DRAIN TEMP | METAL | 1 | 88.9x20 | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0
60HAH14CT001 | 60HAH14CT001 | TT | BP LOWER FRONT HDR DRAIN TEMP | METAL | 1 |  | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH26CT001 | 60HAH26CT001 | TYPE-K TC | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | 457.2x75 | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- |  | 100 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH14CT002 | 60HAH14CT002 | TT | BP LOWER REAR HDR DRAIN TEMP | METAL | 1 |  | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH26CT002 | 60HAH26CT002 | TYPE-K TC | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | 457.2x75 | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- |  | 100 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH26CT001 | 60HAH26CT001 | TT | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | -- | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH71CT001 | 60HAH71CT001 | TYPE-K TC | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH26CT002 | 60HAH26CT002 | TT | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | -- | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH33CT001 to 006 | 60HAH33CT001 to 006 | TYPE-K TC | SH FRONT PLATEN INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH34CT001 to 085 | 60HAH34CT001 to 085 | TYPE-K TC | SH PLATEN FRONT S-27 TUBE TEMP | METAL | 85 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=578 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH34CT086 to 101 | 60HAH34CT086 to 101 | TYPE-K TC | SH PLATEN FRONT TUBE INSIDE GAS PATH TEMP | METAL | 16 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH35CT001 to 012 | 60HAH35CT001 to 012 | TYPE-K TC | SH FONT PLATEN OUTLET HEADER METAL TEMP | METAL | 12 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60LAE70CP501 | 60LAE70CP501 | PI | SH / DSH STAGE-I SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 335.25 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE70CP401 | 60LAE70CP401 | PP | SH / DSH STAGE-I SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 335.25 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60LAE70CT501 | 60LAE70CT501 | TI | SH / DSH STAGE-I SPRAY WATER TEMP | WATER | 1 | 163.3x26 | 335.25 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 15 | 100 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60LAE71CP501 | 60LAE71CP501 | PI | SH / DSH STAGE-I "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE71CP001 | 60LAE71CP001 | PT | SH / DSH STAGE-I "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH71CT002 | 60HAH71CT002 | TYPE-K TC | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LAE71CT001 | 60LAE71CT001 | TT | SH / DSH STAGE-I "A" SPRAY WATER TEMP | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE71CF501 | 60LAE71CF501 | FE | SH / DSH STAGE-I "A" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60LAE71CF001 | 60LAE71CF001 | FT | SH / DSH STAGE-I "A" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE71CF002 | 60LAE71CF002 | FT | SH / DSH STAGE-I "A" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE72CP501 | 60LAE72CP501 | PI | SH / DSH STAGE-I "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE72CP001 | 60LAE72CP001 | PT | SH / DSH STAGE-I "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH71CT003 | 60HAH71CT003 | TYPE-K TC | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LAE72CT001 | 60LAE72CT001 | TT | SH / DSH STAGE-I "B" SPRAY WATER TEMP | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE72CF501 | 60LAE72CF501 | FE | SH / DSH STAGE-I "B" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60LAE72CF001 | 60LAE72CF001 | FT | SH / DSH STAGE-I "B" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE72CF002 | 60LAE72CF002 | FT | SH / DSH STAGE-I "B" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60HAH71CT004 | 60HAH71CT004 | TYPE-K TC | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH71CT001 | 60HAH71CT001 | TT | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH71CT005 | 60HAH71CT005 | TYPE-K TC | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH71CT002 | 60HAH71CT002 | TT | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH71CT401 | 60HAH71CT401 | TW | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH72CT001 | 60HAH72CT001 | TYPE-K TC | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH72CT001 | 60HAH72CT001 | TT | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT002 | 60HAH72CT002 | TYPE-K TC | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH72CT002 | 60HAH72CT002 | TT | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT401 | 60HAH72CT401 | TW | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH71CP001 | 60HAH71CP001 | PT | SH / DSH STAGE-I "A" OUTLET PRESS | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH71CT402 | 60HAH71CT402 | TW | SH / DSH STAGE-I "A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH72CT003 | 60HAH72CT003 | TYPE-K TC | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH71CT003 | 60HAH71CT003 | TT | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT004 | 60HAH72CT004 | TYPE-K TC | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH71CT004 | 60HAH71CT004 | TT | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT005 | 60HAH72CT005 | TYPE-K TC | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH71CT005 | 60HAH71CT005 | TT | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CP001 | 60HAH72CP001 | PT | SH / DSH STAGE-I "B" OUTLET PRESS | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH72CT402 | 60HAH72CT402 | TW | SH / DSH STAGE-I "B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH91CT001 | 60HAH91CT001 | TYPE-K TC | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH72CT003 | 60HAH72CT003 | TT | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH91CT002 | 60HAH91CT002 | TYPE-K TC | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH72CT004 | 60HAH72CT004 | TT | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH91CT003 | 60HAH91CT003 | TYPE-K TC | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH72CT005 | 60HAH72CT005 | TT | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH37CT001 to 006 | 60HAH37CT001 to 006 | TYPE-K TC | SH REAR PLATEN INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH36CT001 to 085 | 60HAH36CT001 to 085 | TYPE-K TC | SH PLATEN REAR S-33 TUBE TEMP | METAL | 85 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=626 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH36CT086 to 101 | 60HAH36CT086 to 101 | TYPE-K TC | SH REAR PLATEN TUBE INSIDE GAS PASS TEMP | METAL | 16 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH38CT001 to 012 | 60HAH38CT001 to 012 | TYPE-K TC | SH REAR PLATEN OUTLET HEADER METAL TEMP | METAL | 12 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60LAE90CP501 | 60LAE90CP501 | PI | SH / DSH STAGE-II SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 334.9 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE90CP401 | 60LAE90CP401 | PP | SH / DSH STAGE-II SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 334.9 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60LAE90CT501 | 60LAE90CT501 | TI | SH / DSH STAGE-II SPRAY WATER TEMP | WATER | 1 | 168.3x26 | 334.9 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 15 | 100 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60LAE91CP501 | 60LAE91CP501 | PI | SH / DSH STAGE-II "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE91CP001 | 60LAE91CP001 | PT | SH / DSH STAGE-II "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH91CT004 | 60HAH91CT004 | TYPE-K TC | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LAE91CT001 | 60LAE91CT001 | TT | SH / DSH STAGE-II "A" SPRAY WATER TEMP | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE91CF501 | 60LAE91CF501 | FE | SH / DSH STAGE-II "A" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60LAE91CF001 | 60LAE91CF001 | FT | SH / DSH STAGE-II "A" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE91CF002 | 60LAE91CF002 | FT | SH / DSH STAGE-II "A" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE92CP501 | 60LAE92CP501 | PI | SH / DSH STAGE-II "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE92CP001 | 60LAE92CP001 | PT | SH / DSH STAGE-II "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH91CT005 | 60HAH91CT005 | TYPE-K TC | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LAE92CT001 | 60LAE92CT001 | TT | SH / DSH STAGE-II "B" SPRAY WATER TEMP | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE92CF501 | 60LAE92CF501 | FE | SH / DSH STAGE-II "B" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60LAE92CF001 | 60LAE92CF001 | FT | SH / DSH STAGE-II "B" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE92CF002 | 60LAE92CF002 | FT | SH / DSH STAGE-II "B" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60HAH92CT001 | 60HAH92CT001 | TYPE-K TC | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH91CT001 | 60HAH91CT001 | TT | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CT002 | 60HAH92CT002 | TYPE-K TC | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH91CT002 | 60HAH91CT002 | TT | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH91CT401 | 60HAH91CT401 | TW | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH92CT003 | 60HAH92CT003 | TYPE-K TC | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH92CT001 | 60HAH92CT001 | TT | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CT004 | 60HAH92CT004 | TYPE-K TC | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH92CT002 | 60HAH92CT002 | TT | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CT401 | 60HAH92CT401 | TW | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH91CP001 | 60HAH91CP001 | PT | SH / DSH STAGE-II"A" OUTLET PRESS | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH91CT402 | 60HAH91CT402 | TW | SH / DSH STAGE-II "A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAH92CT005 | 60HAH92CT005 | TYPE-K TC | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH91CT003 | 60HAH91CT003 | TT | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT001 | 60HAJ21CT001 | TYPE-K TC | RH / DSH "A" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH91CT004 | 60HAH91CT004 | TT | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT002 | 60HAJ21CT002 | TYPE-K TC | RH / DSH "A" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH91CT005 | 60HAH91CT005 | TT | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CP001 | 60HAH92CP001 | PT | SH / DSH STAGE-II"B" OUTLET PRESS | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60HAH92CT402 | 60HAH92CT402 | TW | SH / DSH STAGE-II "B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAJ21CT003 | 60HAJ21CT003 | TYPE-K TC | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH92CT003 | 60HAH92CT003 | TT | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT004 | 60HAJ21CT004 | TYPE-K TC | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH92CT004 | 60HAH92CT004 | TT | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT005 | 60HAJ21CT005 | TYPE-K TC | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60HAH92CT005 | 60HAH92CT005 | TT | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH39CT001 to 006 | 60HAH39CT001 to 006 | TYPE-K TC | SH FINISH INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH40CT001 to 104 | 60HAH40CT001 to 104 | TYPE-K TC | SH FINISH INLET TUBE OUTSIDE FLUE GAS PATH METAL TEMP | METAL | 104 | -- | -- | -- | kg/cm² | -- | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH41CT001 to 134 | 60HAH41CT001 to 134 | TYPE-K TC | SH FINISH OUTLET TUBE OUTSIDE FLUE GAS PATH METAL TEMP | METAL | 134 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=644 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH41CT135 to 152 | 60HAH41CT135 to 152 | TYPE-K TC | SH FINISH OUTLET TUBE INSIDE FLUE GAS PATH METAL TEMP | METAL | 18 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH42CT001 to 009 | 60HAH42CT001 to 009 | TYPE-K TC | SH FINISH OUTLET HEADER-1 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH42CT010 to 015 | 60HAH42CT010 to 015 | TYPE-K TC | SH FINISH OUTLET HEADER-1 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-1 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAH42CT016 to 024 | 60HAH42CT016 to 024 | TYPE-K TC | SH FINISH OUTLET HEADER-2 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH42CT025 to 030 | 60HAH42CT025 to 030 | TYPE-K TC | SH FINISH OUTLET HEADER-2 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-2 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAH42CT031 to 039 | 60HAH42CT031 to 039 | TYPE-K TC | SH FINISH OUTLET HEADER-3 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH42CT040 to 045 | 60HAH42CT040 to 045 | TYPE-K TC | SH FINISH OUTLET HEADER-3 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-3 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAH42CT046 to 054 | 60HAH42CT046 to 054 | TYPE-K TC | SH FINISH OUTLET HEADER-4 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAH42CT055 to 060 | 60HAH42CT055 to 060 | TYPE-K TC | SH FINISH OUTLET HEADER-4 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-4 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAJ22CT001 | 60HAJ22CT001 | TYPE-K TC | RH / DSH "B" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LBA11CT001 | 60LBA11CT001 | TT | SH FINISH OUTLET VENT-1 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ22CT002 | 60HAJ22CT002 | TYPE-K TC | RH / DSH "B" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LBA11CT002 | 60LBA11CT002 | TT | SH FINISH OUTLET VENT-2 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ22CT003 | 60HAJ22CT003 | TYPE-K TC | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LBA12CT001 | 60LBA12CT001 | TT | SH FINISH OUTLET VENT-3 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ22CT004 | 60HAJ22CT004 | TYPE-K TC | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LBA12CT002 | 60LBA12CT002 | TT | SH FINISH OUTLET VENT-4 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBA11CP001 | 60LBA11CP001 | PT | FINAL SH OUTLET PRESSURE - LEFT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 0 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA11CP002 | 60LBA11CP002 | PT | FINAL SH OUTLET PRESSURE - LEFT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 0 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA11CP003 | 60LBA11CP003 | PT | FINAL SH OUTLET PRESSURE - LEFT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 0 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA12CP001 | 60LBA12CP001 | PT | FINAL SH OUTLET PRESSURE - RIGHT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 0 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA12CP002 | 60LBA12CP002 | PT | FINAL SH OUTLET PRESSURE - RIGHT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 0 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA12CP003 | 60LBA12CP003 | PT | FINAL SH OUTLET PRESSURE - RIGHT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 0 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60HAJ22CT005 | 60HAJ22CT005 | TYPE-K TC | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | FLEXIBLE T/C = 30m
60LBA11CT003 | 60LBA11CT003 | TT | SH ERV LEFT-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAB91CT001 | 60LAB91CT001 | TYPE-K TC | FEED WATER LINE DRAIN | METAL | 1 | 33.4x6.35 |  |  | kg/cm² |  |  | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | P | 0
60LBA12CT003 | 60LBA12CT003 | TT | SH ERV RIGHT-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE21CT001 | 60LAE21CT001 | TYPE-K TC | RH / DSH "A" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 0
60LBA11CT004 | 60LBA11CT004 | TT | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE22CT001 | 60LAE22CT001 | TYPE-K TC | RH / DSH "B" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 0
60LBA12CT004 | 60LBA12CT004 | TT | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE71CT001 | 60LAE71CT001 | TYPE-K TC | SH / DSH STAGE-I "A" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0
60LBA11CT005 | 60LBA11CT005 | TT | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE72CT001 | 60LAE72CT001 | TYPE-K TC | SH / DSH STAGE-I "B" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0
60LBA12CT005 | 60LBA12CT005 | TT | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE91CT001 | 60LAE91CT001 | TYPE-K TC | SH / DSH STAGE-II "A" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0
60LBC11CT001 | 60LBC11CT001 | TT | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE92CT001 | 60LAE92CT001 | TYPE-K TC | SH / DSH STAGE-II "B" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 0
60LBC11CT002 | 60LBC11CT002 | TT | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBA11CT001 | 60LBA11CT001 | TYPE-K TC | SH FINISH OUTLET VENT-1 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBC12CT001 | 60LBC12CT001 | TT | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBA11CT002 | 60LBA11CT002 | TYPE-K TC | SH FINISH OUTLET VENT-2 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBC12CT002 | 60LBC12CT002 | TT | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ06CT001 to 006 | 60HAJ06CT001 to 006 | TYPE-K TC | LTRH INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAJ07CT001 to 140 | 60HAJ07CT001 to 140 | TYPE-K TC | LTRH R-04 TUBE OUSIDE FLUE GAS METAL TEMP | METAL | 140 | -- | -- | -- | kg/cm² | -- | <614 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=614 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAJ07CT141 to 158 | 60HAJ07CT141 to 158 | TYPE-K TC | LTRH R-04 TUBE INSIDE FLUE GAS METAL TEMP | METAL | 18 | -- | -- | -- | kg/cm² | -- | <614 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAJ08CT001 to 006 | 60HAJ08CT001 to 006 | TYPE-K TC | LTRH OUTLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <614 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60LAE20CP501 | 60LAE20CP501 | PI | RH SPRAY WATER PRESS | WATER | 1 | 114.3x13.49 | 156.182 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE20CP401 | 60LAE20CP401 | PP | RH SPRAY WATER PRESS | WATER | 1 | 114.3x13.49 | 156.182 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60LAE20CT501 | 60LAE20CT501 | TI | RH SPRAY WATER TEMP | WATER | 1 | 114.3x13.49 | 156.182 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | 10 | 100 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60LAE21CP501 | 60LAE21CP501 | PI | RH / DSH "A" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE21CP001 | 60LAE21CP001 | PT | RH / DSH "A" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60LBA11CT003 | 60LBA11CT003 | TYPE-K TC | SH ERV LEFT-VENT TEMP | METAL | 1 | 114.3 X 6.02 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LAE21CT001 | 60LAE21CT001 | TT | RH / DSH "A" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE21CF501 | 60LAE21CF501 | FE | RH / DSH "A" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60LAE21CF001 | 60LAE21CF001 | FT | RH / DSH "A" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE21CF002 | 60LAE21CF002 | FT | RH / DSH "A" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE22CP501 | 60LAE22CP501 | PI | RH / DSH 'B" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60LAE22CP001 | 60LAE22CP001 | PT | RH / DSH "B" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60LBA11CT004 | 60LBA11CT004 | TYPE-K TC | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LAE22CT001 | 60LAE22CT001 | TT | RH / DSH "B" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE22CF501 | 60LAE22CF501 | FE | RH / DSH "B" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60LAE22CF001 | 60LAE22CF001 | FT | RH / DSH "B" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LAE22CF002 | 60LAE22CF002 | FT | RH / DSH "B" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 0 |  | HART
60LBA11CT005 | 60LBA11CT005 | TYPE-K TC | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ21CT001 | 60HAJ21CT001 | TT | RH / DSH "A" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBA12CT001 | 60LBA12CT001 | TYPE-K TC | SH FINISH OUTLET VENT-3 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ21CT002 | 60HAJ21CT002 | TT | RH / DSH "A" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT401 | 60HAJ21CT401 | TW | RH / DSH "A" INLET TEMP | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60LBA12CT002 | 60LBA12CT002 | TYPE-K TC | SH FINISH OUTLET VENT-4 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ22CT001 | 60HAJ22CT001 | TT | RH / DSH "B" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBA12CT003 | 60LBA12CT003 | TYPE-K TC | SH ERV RIGHT-VENT TEMP | METAL | 1 | 114.3 X 6.02 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ22CT002 | 60HAJ22CT002 | TT | RH / DSH "B" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ22CT401 | 60HAJ22CT401 | TW | RH / DSH "B" INLET TEMP | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAJ21CP001 | 60HAJ21CP001 | PT | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 100 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60LBA12CT004 | 60LBA12CT004 | TYPE-K TC | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ21CT003 | 60HAJ21CT003 | TT | RH / DSH "A" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBA12CT005 | 60LBA12CT005 | TYPE-K TC | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ21CT004 | 60HAJ21CT004 | TT | RH / DSH "A" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBB11CT001 | 60LBB11CT001 | TYPE-K TC | RH OUTLET LEFT- VENT TEMP | METAL | 1 | 76.2 X 5.08 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ21CT005 | 60HAJ21CT005 | TT | RH / DSH "A" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT402 | 60HAJ21CT402 | TW | RH / DSH "A" OUTLET TEMP | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAJ22CP001 | 60HAJ22CP001 | PT | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 100 | kg/cm² | -- | -- | -- | -- | P | 0 |  | PROFIBUS
60LBB11CT002 | 60LBB11CT002 | TYPE-K TC | RH ERV LEFT- VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ22CT003 | 60HAJ22CT003 | TT | RH / DSH "B" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBB11CT003 | 60LBB11CT003 | TYPE-K TC | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ22CT004 | 60HAJ22CT004 | TT | RH / DSH "B" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBB11CT004 | 60LBB11CT004 | TYPE-K TC | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60HAJ22CT005 | 60HAJ22CT005 | TT | RH / DSH "B" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ22CT402 | 60HAJ22CT402 | TW | RH / DSH "B" OUTLET TEMP | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HAJ28CT001 to 006 | 60HAJ28CT001 to 006 | TYPE-K TC | RH FINISH INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAJ29CT001 to 051 | 60HAJ29CT001 to 051 | TYPE-K TC | RH FINISH INLET TUBE OUTSIDE GAS PATH METAL TEMP | METAL | 51 | -- | -- | -- | kg/cm² | -- | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | °C | 0 to 750 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAJ30CT001 to 090 | 60HAJ30CT001 to 090 | TYPE-K TC | RH FINISH OUTLET TUBE OUTSIDE GAS PATH METAL TEMP | METAL | 90 | -- | -- | -- | kg/cm² | -- | <636 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=636 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAJ30CT091 to 103 | 60HAJ30CT091 to 103 | TYPE-K TC | RH FINISH OUTLET TUBE INSIDE GAS PATH METAL TEMP | METAL | 13 | -- | -- | -- | kg/cm² | -- | <636 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60HAJ31CT001 to 012 | 60HAJ31CT001 to 012 | TYPE-K TC | RH FINISH OUTLET HEADER METAL TEMP | METAL | 12 | -- | -- | -- | kg/cm² | -- | <636 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O
60LBB12CT001 | 60LBB12CT001 | TYPE-K TC | RH OUTLET RIGHT- VENT TEMP | METAL | 1 | 76.2 X 5.08 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB11CT001 | 60LBB11CT001 | TT | RH OUTLET LEFT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT002 | 60LBB12CT002 | TYPE-K TC | RH ERV RIGHT- VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB11CT002 | 60LBB11CT002 | TT | RH ERV LEFT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT003 | 60LBB12CT003 | TYPE-K TC | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB11CT003 | 60LBB11CT003 | TT | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT004 | 60LBB12CT004 | TYPE-K TC | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB11CT004 | 60LBB11CT004 | TT | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT005 | 60LBB12CT005 | TYPE-K TC | RH ERV RIGHT- VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB12CT001 | 60LBB12CT001 | TT | RH OUTLET RIGHT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC11CT001 | 60LBC11CT001 | TYPE-K TC | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB12CT002 | 60LBB12CT002 | TT | RH ERV RIGHT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC11CT002 | 60LBC11CT002 | TYPE-K TC | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB12CT005 | 60LBB12CT005 | TT | RH ERV RIGHT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC12CT001 | 60LBC12CT001 | TYPE-K TC | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB12CT003 | 60LBB12CT003 | TT | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC12CT002 | 60LBC12CT002 | TYPE-K TC | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 0
60LBB12CT004 | 60LBB12CT004 | TT | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB01CT501 | 60HCB01CT501 | TI | SB RH STM TEMP (BEFORE PRV) | STEAM | 1 | 114.3x6.02 | 64.6 | 75 | kg/cm² | 374 | 400 | °C | -- | -- | -- | 30 | 140 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 1
60HCB01CP401 | 60HCB01CP401 | PP | SB RH STM PRESS (BEFORE PRV) | STEAM | 1 | 114.3x6.02 | 64.6 | 75 | kg/cm² | 374 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HCB01CP501 | 60HCB01CP501 | PI | SB RH STM PRESS (BEFORE PRV) | STEAM | 1 | 114.3x6.02 | 64.6 | 75 | kg/cm² | 374 | 400 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB03CT501 | 60HCB03CT501 | TI | SB SH STM TEMP (BEFORE PRV) | STEAM | 1 | 127x20 | 295.8 | 308.7 | kg/cm² | 516 | 537 | °C | -- | -- | -- | 21.28 | 220 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 0
60HCB03CP401 | 60HCB03CP401 | PP | SB SH STM PRESS (BEFORE PRV) | STEAM | 1 | 127x20 | 295.8 | 308.7 | kg/cm² | 516 | 537 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HCB03CP501 | 60HCB03CP501 | PI | SB SH STM PRESS (BEFORE PRV) | STEAM | 1 | 127x20 | 295.8 | 308.7 | kg/cm² | 516 | 537 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB01CP001 | 60HCB01CP001 | PT | SB STM PRESS (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Low=18.4 | kg/cm² | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 0 |  | PROFIBUS
60HCB01CP002 | 60HCB01CP002 | PT | SB STM PRESS (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Low=18.4 | kg/cm² | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 0 |  | PROFIBUS
60HCB01CP502 | 60HCB01CP502 | PI | SB STM PRESS (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB01CT001 | 60HCB01CT001 | TYPE-K TC | SB STM TEMP (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 58 | 220 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB01CT001 | 60HCB01CT001 | TT | SB STM TEMP (AFTER PRV) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,A | Low Alarm= 290 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB01CT401 | 60HCB01CT401 | TW | SB STM TEMP (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
60HCB01CF501 | 60HCB01CF501 | FE | SOOTBLOWER STM FLOW | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | 22 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60HCB01CF001 | 60HCB01CF001 | FIT | SOOTBLOWER STM FLOW | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 22 | -- | t/hr | -- | -- | SB/I | -- | -- | Later | mmWC | 0-28 | t/hr | -- | -- | E | 0 |  | PROFIBUS
60HCB13CP501 | 60HCB13CP501 | PI | SB STM PRESS (LRSB LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB13CF501 | 60HCB13CF501 | FE | SOOTBLOWER STM FLOW (LRSB LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60HCB13CF001 | 60HCB13CF001 | FIT | SOOTBLOWER STM FLOW (LRSB LINE-RIGHT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | SB/I,N | Low=2.37 | t/hr | Later | mmWC | 0-9 | t/hr | -- | -- | E | 0 |  | PROFIBUS
60HCB13CT001 | 60HCB13CT001 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB13CT001 | 60HCB13CT001 | TT | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB13CT002 | 60HCB13CT002 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB13CT002 | 60HCB13CT002 | TT | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB13CT003 | 60HCB13CT003 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB13CT003 | 60HCB13CT003 | TT | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB14CP501 | 60HCB14CP501 | PI | SB STM PRESS (LRSB LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB14CF501 | 60HCB14CF501 | FE | SOOTBLOWER STM FLOW (LRSB LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60HCB14CF001 | 60HCB14CF001 | FIT | SOOTBLOWER STM FLOW (LRSB LINE-LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | SB/I,N | Low=2.37 | t/hr | Later | mmWC | 0-9 | t/hr | -- | -- | E | 0 |  | PROFIBUS
60HCB14CT001 | 60HCB14CT001 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB14CT001 | 60HCB14CT001 | TT | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB14CT002 | 60HCB14CT002 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB14CT002 | 60HCB14CT002 | TT | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB14CT003 | 60HCB14CT003 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB14CT003 | 60HCB14CT003 | TT | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB06CP501 | 60HCB06CP501 | PI | APH "A" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB06CP001 | 60HCB06CP001 | PT | APH "A" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 0 |  | PROFIBUS
60HCB05CP501 | 60HCB05CP501 | PI | APH "A" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB05CP001 | 60HCB05CP001 | PT | APH "A" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 0 |  | PROFIBUS
60HCB07CT001 | 60HCB07CT001 | TYPE-K TC | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB07CT001 | 60HCB07CT001 | TT | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB07CT002 | 60HCB07CT002 | TYPE-K TC | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB07CT002 | 60HCB07CT002 | TT | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB07CT003 | 60HCB07CT003 | TYPE-K TC | SB CNDS TEMP (APH "A"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB07CT003 | 60HCB07CT003 | TT | SB CNDS TEMP (APH "A"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB09CP501 | 60HCB09CP501 | PI | APH "B" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB09CP001 | 60HCB09CP001 | PT | APH "B" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 0 |  | PROFIBUS
60HCB08CP501 | 60HCB08CP501 | PI | APH "B" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB08CP001 | 60HCB08CP001 | PT | APH "B" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 0 |  | PROFIBUS
60HCB10CT001 | 60HCB10CT001 | TYPE-K TC | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB10CT001 | 60HCB10CT001 | TT | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB10CT002 | 60HCB10CT002 | TYPE-K TC | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB10CT002 | 60HCB10CT002 | TT | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB10CT003 | 60HCB10CT003 | TYPE-K TC | SB CNDS TEMP (APH "B"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB10CT003 | 60HCB10CT003 | TT | SB CNDS TEMP (APH "B"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB11CP501 | 60HCB11CP501 | PI | SB STM PRESS (WB LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB11CF501 | 60HCB11CF501 | FE | SOOTBLOWER STM FLOW (WB LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60HCB11CF001 | 60HCB11CF001 | FIT | SOOTBLOWER STM FLOW (WB LINE-FRONT & LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | SB/I,N | Low=1.8 | t/hr | Later | mmWC | 0-4 | t/hr | -- | -- | E | 0 |  | PROFIBUS
60HCB11CT001 | 60HCB11CT001 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB11CT001 | 60HCB11CT001 | TT | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB11CT002 | 60HCB11CT002 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB11CT002 | 60HCB11CT002 | TT | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB11CT003 | 60HCB11CT003 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB11CT003 | 60HCB11CT003 | TT | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB12CP501 | 60HCB12CP501 | PI | SB STM PRESS (WB LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 1
60HCB12CF501 | 60HCB12CF501 | FE | SOOTBLOWER STM FLOW (WB LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 0
60HCB12CF001 | 60HCB12CF001 | FIT | SOOTBLOWER STM FLOW (WB LINE-RIGHT & REAR) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | SB/I,N | Low=1.8 | t/hr | Later | mmWC | 0-4 | t/hr | -- | -- | E | 0 |  | PROFIBUS
60HCB12CT001 | 60HCB12CT001 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB12CT001 | 60HCB12CT001 | TT | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB12CT002 | 60HCB12CT002 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB12CT002 | 60HCB12CT002 | TT | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB12CT003 | 60HCB12CT003 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0
60HCB12CT003 | 60HCB12CT003 | TT | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LDN01CP502 | 60LDN01CP502 | PI | DISTRIBUTION LINE PRESSURE | NITROGEN | 1 | 60.3x5.54 | 5 | -- | kg/cm² | Ambient | -- | °C | -- | -- | -- | -- | -- | L/I | -- | -- | -- | -- | -- | -- | -- | 1/2" NPT(M) | V | 1
60LDN01CP501 | 60LDN01CP501 | PI | PRESSURE AT SUPPLY MANIFOLD | NITROGEN | 1 | 60.3x5.54 | 5 | -- | kg/cm² | Ambient | -- | °C | -- | -- | -- | -- | -- | L/I | -- | -- | -- | -- | -- | -- | -- | 1/2" NPT(M) | V | 1
60HFE01CP401 |  | PP | PA FAN "A" INLET AIR PRESS | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 1 | --
60HNA01CL101 |  | LS | ECON OUTLET HOPPER-1 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 513 | mm
60HFE01CT031 |  | PT-100 | PA FAN "A" INLET AIR TEMP | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 3 | --
60HNA01CL103 |  | LS | ECON OUTLET HOPPER-1 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 514 | mm
60HNA01CL102 |  | LS | ECON OUTLET HOPPER-2 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 517 | mm
60HNA01CL104 |  | LS | ECON OUTLET HOPPER-2 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 518 | mm
60HNA02CL101 |  | LS | ECON OUTLET HOPPER-3 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 521 | mm
60HFE05CP401 |  | PP | PA FAN "B" INLET AIR PRESS | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 8 | --
60HNA02CL103 |  | LS | ECON OUTLET HOPPER-3 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 522 | mm
60HFE05CT031 |  | PT-100 | PA FAN "B" INLET AIR TEMP | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 10 | --
60HNA02CL102 |  | LS | ECON OUTLET HOPPER-4 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 525 | mm
60HNA02CL104 |  | LS | ECON OUTLET HOPPER-4 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 526 | mm
60HNA10CL101 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 1- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 547 | mm
60HNA10CL104 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 1- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 548 | mm
60HFE01CY101 |  | VT | PA FAN "A" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 15 | --
60HFE01CT001 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 16 | --
60HFE01CT002 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 17 | --
60HFE01CT003 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 18 | --
60HFE01CT004 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 19 | --
60HFE01CT005 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 20 | --
60HFE01CT006 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 21 | --
60HFE01CT007 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 22 | --
60HFE01CT008 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 23 | --
60HFE01CT009 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 24 | --
60HFE01CT010 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 25 | --
60HFE01CT011 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 26 | --
60HFE01CT012 |  | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 27 | --
60HNA10CL102 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 2- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 551 | mm
60HNA10CL105 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 2- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 552 | mm
60HNA10CL103 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 3- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 555 | mm
60HNA10CL106 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 3- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 556 | mm
60HNA20CL101 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 4- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 559 | mm
60HNA20CL104 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 4- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 560 | mm
60HNA20CL102 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 5- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 563 | mm
60HNA20CL105 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 5- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 564 | mm
60HNA20CL103 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 6- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 567 | mm
60HNA20CL106 |  | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 6- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 568 | mm
60HLD10CL101 |  | LS | AH-A ASH HOPPER-1 - LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 605 | mm
60HLD10CL102 |  | LS | AH-A ASH HOPPER-2- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 606 | mm
60HFE01CY005 |  | VT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 40 | mm/s
60HFE01CY006 |  | VT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 41 | mm/s
60HFE01CT028 |  | PT-100 | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 42 | --
60HFE01CT029 |  | PT-100 | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 43 | --
60HFE01CT030 |  | PT-100 | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 44 | --
60HLD10CL103 |  | LS | AH-A ASH HOPPER-3- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 607 | mm
60HLD10CL104 |  | LS | AH-A FG O/L DUCT HOPPER-1 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 608 | mm
60HLD10CL105 |  | LS | AH-A FG O/L DUCT HOPPER-2 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 609 | mm
60HFE01CY004 |  | VT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 48 | mm/s
60HFE01CY003 |  | VT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 49 | mm/s
60HFE01CY002 |  | VT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 50 | mm/s
60HFE01CY001 |  | VT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 51 | mm/s
60HFE01CT025 |  | PT-100 | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 52 | --
60HFE01CT026 |  | PT-100 | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 53 | --
60HFE01CT027 |  | PT-100 | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 54 | --
60HLD10CL106 |  | LS | AH-A FG O/L DUCT HOPPER-3 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 610 | mm
60HLD10CL107 |  | LS | AH-A ASH HOPPER-1 - LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 611 | mm
60HLD10CL108 |  | LS | AH-A ASH HOPPER-2- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 612 | mm
60HFE01CT013 |  | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 58 | --
60HFE01CT014 |  | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 59 | --
60HFE01CT015 |  | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 60 | --
60HFE01CT016 |  | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 61 | --
60HFE01CT017 |  | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 62 | --
60HFE01CT018 |  | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 63 | --
60HFE01CT019 |  | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 64 | --
60HFE01CT020 |  | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 65 | --
60HFE01CT021 |  | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 66 | --
60HFE01CT022 |  | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 67 | --
60HFE01CT023 |  | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 68 | --
60HFE01CT024 |  | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 69 | --
60HLD10CL109 |  | LS | AH-A ASH HOPPER-3- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 613 | mm
60HLD10CL110 |  | LS | AH-A FG O/L DUCT HOPPER-1 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 614 | mm
60HLD10CL111 |  | LS | AH-A FG O/L DUCT HOPPER-2 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 615 | mm
60HLD10CL112 |  | LS | AH-A FG O/L DUCT HOPPER-3 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 616 | mm
60HLD20CL101 |  | LS | AH-B ASH HOPPER-1 - LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 617 | mm
60HLD20CL102 |  | LS | AH-B ASH HOPPER-2- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 618 | mm
60HLD20CL103 |  | LS | AH-B ASH HOPPER-3- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 619 | mm
60HLD20CL104 |  | LS | AH-B FG O/L DUCT HOPPER-1 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 620 | mm
60HLD20CL105 |  | LS | AH-B FG O/L DUCT HOPPER-2 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 621 | mm
60HFE05CY101 |  | VT | PA FAN "B" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 79 | --
60HFE05CT001 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 80 | --
60HFE05CT002 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 81 | --
60HFE05CT003 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 82 | --
60HFE05CT004 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 83 | --
60HFE05CT005 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 84 | --
60HFE05CT006 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 85 | --
60HFE05CT007 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 86 | --
60HFE05CT008 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 87 | --
60HFE05CT009 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 88 | --
60HFE05CT010 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 89 | --
60HFE05CT011 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 90 | --
60HFE05CT012 |  | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 91 | --
60HLD20CL106 |  | LS | AH-B FG O/L DUCT HOPPER-3 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COI | -- | T | 0 | ** Vertical distance from top of hopper | - | 622 | mm
60HLD20CL107 |  | LS | AH-B ASH HOPPER-1 - LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 623 | mm
60HLD20CL108 |  | LS | AH-B ASH HOPPER-2- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 624 | mm
60HLD20CL109 |  | LS | AH-B ASH HOPPER-3- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 625 | mm
60HLD20CL110 |  | LS | AH-B FG O/L DUCT HOPPER-1 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 626 | mm
60HLD20CL111 |  | LS | AH-B FG O/L DUCT HOPPER-2 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 627 | mm
60HLD20CL112 |  | LS | AH-B FG O/L DUCT HOPPER-3 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later |  | -- | -- | -- | -- | COD | -- | T | 0 | ** Vertical distance from top of hopper | - | 628 | mm
60HLD10CT005 |  | TT | AH-A FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 638 | --
60HLD10CT006 |  | TT | AH-A FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 640 | --
60HLD20CT005 |  | TT | AH-B FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 650 | --
60HLD20CT006 |  | TT | AH-B FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 652 | --
60HNA50CL001-008 |  | LT | DUCT ASH LEVEL MEASUREMENT - APH OUTLET (ESP INLET DUCT ASH LEVEL MEASUREMENT) | FLUE GAS | 8 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 13 | -- | D/I | -- |  |  |  | 4 to 20 | mA | -- | -- | T | 1 |  | HART | 679 | --
60HFE05CY005 |  | VT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 104 | mm/s
60HFE05CY006 |  | VT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 105 | mm/s
60HFE05CT028 |  | PT-100 | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 106 | --
60HFE05CT029 |  | PT-100 | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 107 | --
60HFE05CT030 |  | PT-100 | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 108 | --
60HNA10CL001, 60HNA20CL001 |  | LT | ECO OUTLET DUCT ASH LEVEL MEASUREMENT | FLUE GAS | 2 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 13 | -- | D/I | -- |  |  |  | 4 to 20 | mA | -- | -- | T | 1 |  | HART | 680 | --
60HNC10CT033 |  | TT | ID FAN "A" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** |  | ** | ** | -- | -- | -- | -- | E | 0 | ** BY BHEL RANIPET/EDN | PROFIBUS | 781 | **
60HNC10CT032 |  | TT | ID FAN "A" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** |  | ** | ** | -- | -- | -- | -- | E | 0 | ** BY BHEL RANIPET/EDN | PROFIBUS | 783 | **
60HFE05CY004 |  | VT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 112 | mm/s
60HFE05CY003 |  | VT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 113 | mm/s
60HFE05CY002 |  | VT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 114 | mm/s
60HFE05CY001 |  | VT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 115 | mm/s
60HFE05CT025 |  | PT-100 | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 116 | --
60HFE05CT026 |  | PT-100 | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 117 | --
60HFE05CT027 |  | PT-100 | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 118 | --
60HNC20CT033 |  | TT | ID FAN "B" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** |  | ** | ** | -- | -- | -- | -- | E | 0 | ** BY BHEL RANIPET/EDN | PROFIBUS | 849 | **
60HNC20CT032 |  | TT | ID FAN "B" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** |  | ** | ** | -- | -- | -- | -- | E | 0 | ** BY BHEL RANIPET/EDN | PROFIBUS | 851 | **
60HNC12CQ001 |  | AT | ID FAN "A" COLD FLUE GAS OUTLET O2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 899 | --
60HFE05CT013 |  | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 122 | --
60HFE05CT014 |  | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 123 | --
60HFE05CT015 |  | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 124 | --
60HFE05CT016 |  | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 125 | --
60HFE05CT017 |  | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 126 | --
60HFE05CT018 |  | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 127 | --
60HFE05CT019 |  | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 128 | --
60HFE05CT020 |  | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 129 | --
60HFE05CT021 |  | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 130 | --
60HFE05CT022 |  | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 131 | --
60HFE05CT023 |  | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 132 | --
60HFE05CT024 |  | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 133 | --
60HNC12CQ002 |  | AT | ID FAN "A" COLD FLUE GAS OUTLET CO2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C |  | -- | % by dry volume | -- | -- | D/I | -- |  |  | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 900 | --
60HNC22CQ001 |  | AT | ID FAN "B" COLD FLUE GAS OUTLET O2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 907 | --
60HNC22CQ002 |  | AT | ID FAN "B" COLD FLUE GAS OUTLET CO2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C |  | -- | % by dry volume | -- | -- | D/I | -- |  |  | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 908 | --
60HNC30CQ007 |  | AT | FLUE GAS TO STACK O2 | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 917 | --
60HAD20CW001 |  |  | FRONT WALL - LOAD CELL 1 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 996 | --
60HAD20CW002 |  |  | FRONT WALL - LOAD CELL 2 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 997 | --
60HAD20CW003 |  |  | FRONT WALL - LOAD CELL 3 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 998 | --
60HAD20CW004 |  |  | FRONT WALL - LOAD CELL 4 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 999 | --
60HAD20CW005 |  |  | FRONT WALL - LOAD CELL 5 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1000 | --
60HFE02CT001 |  | PT-100 | PA FAN "A" OUTLET AIR TEMP | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 143 | --
60HFE06CT001 |  | PT-100 | PA FAN "B" OUTLET AIR TEMP | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 144 | --
60HAD20CW006 |  |  | FRONT WALL - LOAD CELL 6 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1001 | --
60HAD20CW007 |  |  | FRONT WALL - LOAD CELL 7 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1002 | --
60HFE02CP501 |  | PI | PA FAN "A" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 147 | --
60HFE06CP501 |  | PI | PA FAN "B" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 148 | --
60HFE02CP401 |  | PP | PA FAN "A" OUTLET AIR PRESS | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 149 | --
60HFE06CP401 |  | PP | PA FAN "B" OUTLET AIR PRESS | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 150 | --
60HFE02CT401 |  | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 151 | --
60HFE06CT401 |  | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 152 | --
60HFE02CT402 |  | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 153 | --
60HFE06CT402 |  | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 154 | --
60HFE02CT403 |  | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 155 | --
60HFE06CT403 |  | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 156 | --
60HFE02CT404 |  | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 157 | --
60HFE06CT404 |  | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 158 | --
60HFE02CT405 |  | TP | APH "A" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 159 | --
60HFE02CT406 |  | TP | APH "A" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 160 | --
60HFE02CT407 |  | TP | APH "A" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 161 | --
60HFE02CP402 |  | PP | APH "A" INLET COLD PA PRESS | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 162 | --
60HAD20CW008 |  |  | FRONT WALL - LOAD CELL 8 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1003 | --
60HAD30CW001 |  |  | REAR WALL - LOAD CELL 1 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1004 | --
60HFE06CT405 |  | TP | APH "B" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 165 | --
60HFE06CT406 |  | TP | APH "B" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 166 | --
60HFE06CT407 |  | TP | APH "B" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 167 | --
60HFE06CP402 |  | PP | APH "B" INLET COLD PA PRESS | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 168 | --
60HAD30CW002 |  |  | REAR WALL - LOAD CELL 2 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1005 | --
60HAD30CW003 |  |  | REAR WALL - LOAD CELL 3 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1006 | --
60HFE03CT401 |  | TP | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 171 | --
60HFE03CT402 |  | TP | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 172 | --
60HFE03CT403 |  | TP | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 173 | --
60HFE03CP401 |  | PP | APH "A" HOT PA PRESS | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 174 | --
60HFE03CT001 |  | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 175 | --
60HFE03CT002 |  | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 176 | --
60HFE03CT003 |  | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 177 | --
60HFE03CT004 |  | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 178 | --
60HAD30CW004 |  |  | REAR WALL - LOAD CELL 4 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1007 | --
60HAD30CW005 |  |  | REAR WALL - LOAD CELL 5 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1008 | --
60HAD30CW006 |  |  | REAR WALL - LOAD CELL 6 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1009 | --
60HAD30CW007 |  |  | REAR WALL - LOAD CELL 7 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1010 | --
60HAD30CW008 |  |  | REAR WALL - LOAD CELL 8 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- |  | 4-20 | mA | -- | -- | -- | -- | T | 0 |  | - | 1011 | --
60HFE01CG001 |  | APT | PA FAN - A ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- |  | 4-20 | mA | 0-100 | % | -- | -- | R | 0 |  | - | 1016 | --
60HFE07CT401 |  | TP | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 185 | --
60HFE07CT402 |  | TP | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 186 | --
60HFE07CT403 |  | TP | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 187 | --
60HFE07CP401 |  | PP | APH "B" HOT PA PRESS | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 188 | --
60HFE07CT001 |  | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 189 | --
60HFE07CT002 |  | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 190 | --
60HFE07CT003 |  | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 191 | --
60HFE07CT004 |  | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 192 | --
60HFE05CG001 |  | APT | PA FAN - B ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- |  | 4-20 | mA | 0-100 | % | -- | -- | R | 0 |  | - | 1017 | --
60HBK15CG001-009 60HBK25CG001-009 60HBK35CG001-004 60HBK45CG001-004 60HBK10CG001 60HBK30CG001 |  |  | FURNACE THERMAL EXPANSION MEASUREMENT | DISPLACEMENT | 28 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I |  |  | 4-20 | mA |  |  |  | -- | T | 1 |  |  | 1023
60HBK10CP002 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  |  | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 426 | --
60HFE01CT031 |  | TT | PA FAN "A" INLET AIR TEMP | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART | 4 | --
60HFE01CP002 |  | PDT | PA FAN "A" DP ACROSS SUCTION & IMPELLER | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 5 | --
60HFE01CP003 |  | PDT | PA FAN "A" STALL DETECTION PROBE | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 6 | mmWC
60HBK10CP004 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  |  | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 428 | --
60HBK30CP002 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  |  | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 430 | --
60HFE10CP003 |  | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | F/N,A | ## |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 | ## Mill start permissive >635mmWC, <635mmWC mill trip with 5s delay, 508mmWC immediate mill trip | HART | 201 | mmWC
60HFE10CP004 |  | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | F/N,A | ## |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 | ## Mill start permissive >635mmWC, <635mmWC mill trip with 5s delay, 508mmWC immediate mill trip | HART | 202 | mmWC
60HFE10CP005 |  | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | F/N,A | ## |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 | ## Mill start permissive >635mmWC, <635mmWC mill trip with 5s delay, 508mmWC immediate mill trip | HART | 203 | mmWC
60HFE05CT031 |  | TT | PA FAN "B" INLET AIR TEMP | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART | 11 | --
60HLB10CP401 |  | PP | FD FAN "A" INLET AIR PRESS | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 205 | --
60HFE05CP002 |  | PDT | PA FAN "B" DP ACROSS SUCTION & IMPELLER | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 12 | --
60HLB10CT028 |  | PT-100 | FD FAN "A" INLET AIR TEMP | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 207 | --
60HFE05CP003 |  | PDT | PA FAN "B" STALL DETECTION PROBE | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 13 | mmWC
60HBK30CP003 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  |  | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 431 | --
60HFE01CT001 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 28 | °C
60HFE01CT002 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 29 | °C
60HLB20CP401 |  | PP | FD FAN "B" INLET AIR PRESS | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 212 | --
60HFE01CT003 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 30 | °C
60HLB20CT028 |  | PT-100 | FD FAN "B" INLET AIR TEMP | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 214 | --
60HFE01CT004 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 31 | °C
60HFE01CT005 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 32 | °C
60HFE01CT006 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 33 | °C
60HFE01CT007 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 34 | °C
60HLB10CY101 |  | VT | FD FAN "A" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 219 | --
60HLB10CT001 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 220 | --
60HLB10CT002 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 221 | --
60HLB10CT003 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 222 | --
60HLB10CT004 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 223 | --
60HLB10CT005 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 224 | --
60HLB10CT006 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 225 | --
60HLB10CT007 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 226 | --
60HLB10CT008 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 227 | --
60HLB10CT009 |  | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 228 | --
60HFE01CT008 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 35 | °C
60HFE01CT009 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 36 | °C
60HFE01CT010 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 37 | °C
60HFE01CT011 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 38 | °C
60HFE01CT012 |  | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 39 | °C
60HFE01CT028 |  | TT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 45 | °C
60HFE01CT029 |  | TT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 46 | °C
60HFE01CT030 |  | TT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 47 | °C
60HFE01CT025 |  | TT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 55 | °C
60HLB10CY005 |  | VT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 238 | mm/s
60HLB10CY006 |  | VT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 239 | mm/s
60HLB10CT010 |  | PT-100 | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 240 | --
60HLB10CT011 |  | PT-100 | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 241 | --
60HLB10CT012 |  | PT-100 | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 242 | --
60HFE01CT026 |  | TT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 56 | °C
60HFE01CT027 |  | TT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 57 | °C
60HFE01CT013 |  | TT | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 70 | °C
60HLB10CY004 |  | VT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 246 | mm/s
60HLB10CY003 |  | VT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 247 | mm/s
60HLB10CY002 |  | VT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 248 | mm/s
60HLB10CY001 |  | VT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 249 | mm/s
60HLB10CT025 |  | PT-100 | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 250 | --
60HLB10CT026 |  | PT-100 | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 251 | --
60HLB10CT027 |  | PT-100 | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 252 | --
60HFE01CT014 |  | TT | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 71 | °C
60HFE01CT019/020 |  | TT | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 72 | °C
60HFE01CT015 |  | TT | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 73 | °C
60HLB10CT013 |  | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 256 | --
60HLB10CT014 |  | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 257 | --
60HLB10CT015 |  | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 258 | --
60HLB10CT016 |  | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 259 | --
60HLB10CT017 |  | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 260 | --
60HLB10CT018 |  | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 261 | --
60HLB10CT019 |  | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 262 | --
60HLB10CT020 |  | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 263 | --
60HLB10CT021 |  | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 264 | --
60HLB10CT022 |  | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 265 | --
60HLB10CT023 |  | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 266 | --
60HLB10CT024 |  | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 267 | --
60HFE01CT016 |  | TT | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 74 | °C
60HFE01CT021/022 |  | TT | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 75 | °C
60HFE01CT017 |  | TT | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 76 | °C
60HFE01CT018 |  | TT | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 77 | °C
60HFE01CT023/024 |  | TT | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 78 | °C
60HFE05CT001 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 92 | °C
60HFE05CT002 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 93 | °C
60HFE05CT003 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 94 | °C
60HFE05CT004 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 95 | °C
60HLB20CY101 |  | VT | FD FAN "B" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 277 | --
60HLB20CT001 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 278 | --
60HLB20CT002 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 279 | --
60HLB20CT003 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 280 | --
60HLB20CT004 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 281 | --
60HLB20CT005 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 282 | --
60HLB20CT006 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 283 | --
60HLB20CT007 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 284 | --
60HLB20CT008 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 285 | --
60HLB20CT009 |  | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 286 | --
60HFE05CT005 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 96 | °C
60HFE05CT006 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 97 | °C
60HFE05CT007 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 98 | °C
60HFE05CT008 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 99 | °C
60HFE05CT009 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 100 | °C
60HFE05CT010 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 101 | °C
60HFE05CT011 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 102 | °C
60HFE05CT012 |  | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 103 | °C
60HFE05CT028 |  | TT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 109 | °C
60HLB20CY005 |  | VT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 296 | mm/s
60HLB20CY006 |  | VT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 297 | mm/s
60HLB20CT010 |  | PT-100 | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 298 | --
60HLB20CT011 |  | PT-100 | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 299 | --
60HLB20CT012 |  | PT-100 | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 300 | --
60HFE05CT029 |  | TT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 110 | °C
60HFE05CT030 |  | TT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 111 | °C
60HFE05CT025 |  | TT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 119 | °C
60HLB20CY004 |  | VT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 304 | mm/s
60HLB20CY003 |  | VT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 305 | mm/s
60HLB20CY002 |  | VT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 306 | mm/s
60HLB20CY001 |  | VT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 307 | mm/s
60HLB20CT025 |  | PT-100 | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 308 | --
60HLB20CT026 |  | PT-100 | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 309 | --
60HLB20CT027 |  | PT-100 | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 310 | --
60HFE05CT026 |  | TT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 120 | °C
60HFE05CT027 |  | TT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 121 | °C
60HFE05CT013 |  | TT | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 134 | °C
60HLB20CT013 |  | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 314 | --
60HLB20CT014 |  | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 315 | --
60HLB20CT015 |  | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 316 | --
60HLB20CT016 |  | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 317 | --
60HLB20CT017 |  | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 318 | --
60HLB20CT018 |  | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 319 | --
60HLB20CT019 |  | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 320 | --
60HLB20CT020 |  | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 321 | --
60HLB20CT021 |  | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 322 | --
60HLB20CT022 |  | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 323 | --
60HLB20CT023 |  | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 324 | --
60HLB20CT024 |  | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 325 | --
60HFE05CT014 |  | TT | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 135 | °C
60HFE05CT019/020 |  | TT | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 136 | °C
60HFE05CT015 |  | TT | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 137 | °C
60HFE05CT016 |  | TT | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 138 | °C
60HFE05CT021/022 |  | TT | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 139 | °C
60HFE05CT017 |  | TT | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 140 | °C
60HFE05CT018 |  | TT | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 141 | °C
60HFE05CT023/024 |  | TT | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 142 | °C
60HFE02CT001 |  | TT | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 145 | --
60HLA12CT001 |  | PT-100 | FD FAN "A" OUTLET AIR TEMP | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 335 | --
60HFE06CT001 |  | TT | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 146 | --
60HLA12CT401 |  | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 337 | --
60HLA12CT402 |  | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 338 | --
60HLA12CT403 |  | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 339 | --
60HLA12CT404 |  | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 340 | --
60HLA12CP501 |  | PI | FD FAN "A" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 341 | --
60HLA12CP401 |  | PP | FD FAN "A" OUTLET AIR PRESS | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 342 | --
60HLA22CT001 |  | PT-100 | FD FAN "B" OUTLET AIR TEMP | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 343 | --
60HBK30CP004 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  |  | -1200 to 1200 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | WIDE RANGE PRESSURE TRANSMITTER | PROFIBUS | 432 | --
60HLA22CT401 |  | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 345 | --
60HLA22CT402 |  | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 346 | --
60HLA22CT403 |  | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 347 | --
60HLA22CT404 |  | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 348 | --
60HLA22CP501 |  | PI | FD FAN "B" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 349 | --
60HLA22CP401 |  | PP | FD FAN "B" OUTLET AIR PRESS | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 350 | --
60HLA13CT401 |  | TP | APH "A" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 351 | --
60HLA13CT402 |  | TP | APH "A" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 352 | --
60HLA13CT403 |  | TP | APH "A" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 353 | --
60HLA13CP401 |  | PP | APH "A" INLET COLD SA AIR PRESS | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 354 | --
60HLA13CT001 |  | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 355 | --
60HLA13CT002 |  | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 356 | --
60HLA13CT003 |  | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 357 | --
60HLA13CT004 |  | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 358 | --
60HFE02CP002 |  | PDT | APH "A" COLD TO HOT PA DIFF. PRESS. | PA | 1 | 3450 x 3450 / 3200 x 4300 | 1048 / 1009 | 1385 / 1330 | mmWC | 35 / 323 | 60 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 164 | --
60HBK10CP005 |  | PT | BEFORE REAR PLATEN SH FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 453 | --
60HFE06CP002 |  | PDT | APH "B" COLD TO HOT PA DIFF. PRESS. | PA | 1 | 3450 x 3450 / 3200 x 4300 | 1048 / 1009 | 1385 / 1330 | mmWC | 35 / 323 | 60 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 170 | --
60HFE03CT001 |  | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 179 | --
60HFE03CT002 |  | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 180 | --
60HLA23CT401 |  | TP | APH "B" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 364 | --
60HLA23CT402 |  | TP | APH "B" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 365 | --
60HLA23CT403 |  | TP | APH "B" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 366 | --
60HLA23CP401 |  | PP | APH "B" INLET COLD SA AIR PRESS | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 367 | --
60HLA23CT001 |  | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 368 | --
60HLA23CT002 |  | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 369 | --
60HLA23CT003 |  | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 370 | --
60HLA23CT004 |  | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- |  | 0 to 75 | °C | -- | -- | -- |  | P | 0 |  | - | 371 | --
60HFE03CT003 |  | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 181 | --
60HFE03CT004 |  | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 182 | --
60HBK30CP005 |  | PT | BEFORE REAR PLATEN SH FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 454 | --
60HBK10CP006 |  | PT | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 465 | --
60HFE07CT001 |  | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 193 | --
60HFE07CT002 |  | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 194 | --
60HFE07CT003 |  | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 195 | --
60HFE07CT004 |  | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 196 | --
60HBK30CP006 |  | PT | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 466 | --
60HLA14CT401 |  | TP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 381 | --
60HLA14CT402 |  | TP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 382 | --
60HLA14CT403 |  | TP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 383 | --
60HLA14CP401 |  | PP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 384 | --
60HLA14CT001 |  | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 385 | --
60HLA14CT002 |  | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 386 | --
60HLA14CT003 |  | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 387 | --
60HLA14CT004 |  | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 388 | --
60HBK10CP007 |  | PT | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 475 | --
60HFE10CP001 |  | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | D/I,C | -- |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 199 | --
60HFE10CP002 |  | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | D/I,C | -- |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 200 | --
60HFE10CP006 |  | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | D/I,C | -- |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 204 | --
60HBK30CP007 |  | PT | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 476 | --
60HLB10CT028 |  | TT | FD FAN "A" INLET AIR TEMP | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART | 208 | --
60HLA24CT401 |  | TP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 395 | --
60HLA24CT402 |  | TP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 396 | --
60HLA24CT403 |  | TP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 397 | --
60HLA24CP401 |  | PP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 398 | --
60HLA24CT001 |  | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 399 | --
60HLA24CT002 |  | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 400 | --
60HLA24CT003 |  | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 401 | --
60HLA24CT004 |  | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 402 | --
60HLB10CP002 |  | PDT | FD FAN "A" DP ACROSS SUCTION & IMPELLER | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 209 | --
60HLB10CP003 |  | PDT | FD FAN "A" STALL DETECTION PROBE | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 210 | mmWC
60HBK10CP008 |  | PT | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 485 | --
60HBK30CP008 |  | PT | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 486 | --
60HLB20CT028 |  | TT | FD FAN "B" INLET AIR TEMP | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART | 215 | --
60HLB20CP002 |  | PDT | FD FAN "B" DP ACROSS SUCTION & IMPELLER | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 216 | --
60HLA15CF501 |  | FE | HOT SA "A" AIR | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | DP=99.2 | -- | mmWC | -- | -- | -- | -- |  | -- | -- | -- | -- | -- | -- | T | 0 | Refer FE characteristics | - | 409 | --
60HLB20CP003 |  | PDT | FD FAN "B" STALL DETECTION PROBE | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 217 | mmWC
60HBK10CP009 |  | PT | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 495 | --
60HLA25CF501 |  | FE | HOT SA "B" AIR | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | DP=99.2 | -- | mmWC | -- | -- | -- | -- |  | -- | -- | -- | -- | -- | -- | T | 0 | Refer FE characteristics | - | 412 | --
60HLB10CT001 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 229 | °C
60HLB10CT002 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 230 | °C
60HLA15CT001 |  | TYPE-K TC | HOT SA FROM APH "A" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 415 | --
60HLA15CT002 |  | TYPE-K TC | HOT SA FROM APH "A" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 416 | --
60HLB10CT003 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 231 | °C
60HLB10CT004 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 232 | °C
60HLA15CP401 |  | PP | HOT SA FROM APH "A" PRESS | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 419 | --
60HLA25CT001 |  | TYPE-K TC | HOT SA FROM APH "B" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 420 | --
60HLA25CT002 |  | TYPE-K TC | HOT SA FROM APH "B" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- |  | 0 to 500 | °C | -- | -- | -- |  | P | 0 |  | - | 421 | --
60HLB10CT005 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 233 | °C
60HLB10CT006 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 234 | °C
60HLA25CP401 |  | PP | HOT SA FROM APH 'B" PRESS | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 424 | --
60HBK10CP001 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | F/N,A | ## |  | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 | ## High=76.2, Low= -101.6; Very High=152, Very low= -178; Very very low = -228 | HART | 425 | mmWC
60HLB10CT007 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 235 | °C
60HBK10CP003 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | F/N,A | ## |  | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 | ## High=76.2, Low= -101.6; Very High=152, Very low= -178; Very very low = -228 | HART | 427 | mmWC
60HLB10CT008 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 236 | °C
60HBK30CP001 |  | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | F/N,A | ## |  | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 | ## High=76.2, Low= -101.6; Very High=152, Very low= -178; Very very low = -228 | HART | 429 | mmWC
60HLB10CT009 |  | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 237 | °C
60HLB10CT010 |  | TT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 243 | °C
60HLB10CT011 |  | TT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 244 | °C
60HBK10CP501 |  | PI | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 | FMG | - | 433 | --
60HBK30CP501 |  | PI | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 434 | --
60HBK30CP502 |  | PI | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 | FMG | - | 435 | --
60HBK10CT001 |  | TYPE-K TC | FURNACE TEMP PROBE (LEFT SIDE) | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 1900 | °C | -- | -- | -- | -- | T | 0 |  | - | 436 | --
60HBK30CT001 |  | TYPE-K TC | FURNACE TEMP PROBE (RIGHT SIDE) | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 1900 | °C | -- | -- | -- | -- | T | 0 |  | - | 437 | --
60HLB10CT012 |  | TT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 245 | °C
60HLB10CT025 |  | TT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 253 | °C
60HBK10CT408 |  | TP | FURNACE TEMP | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 440 | --
60HLA18CP501 |  | PI | WINDBOX PRESS (LEFT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 | FMG | - | 441 | --
60HLA28CP501 |  | PI | WINDBOX PRESS (RIGHT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 | FMG | - | 442 | --
60HLB10CT026 |  | TT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 254 | °C
60HLB10CT027 |  | TT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 255 | °C
60HLA18CP001 |  | PDT | FURN TO WINDBOX DIFF PRESS (LEFT SIDE) | FLUE GAS / SA | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 102 | -- | mmWC | -- | -- | SA/I,C,N | High alarm=225 |  | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 |  | HART | 445 | mmWC
60HLA28CP001 |  | PDT | FURN TO WINDBOX DIFF PRESS (RIGHT SIDE) | FLUE GAS / SA | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 102 | -- | mmWC | -- | -- | SA/I,C,N | High alarm=225 |  | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 |  | HART | 446 | mmWC
60HHS10CP001 |  | PDT | SCANNER COOLING AIR / FURN DIFF PRESS | SCA. AIR/FLUE GAS | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 521 | -- | mmWC | -- | -- | F/A,N |  |  | 0 to 800 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 |  | HART | 447 | mmWC
60HHS10CP002 |  | PDT | SCANNER COOLING AIR / FURN DIFF PRESS | SCA. AIR/FLUE GAS | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 521 | -- | mmWC | -- | -- | F/A,N |  |  | 0 to 800 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 0 |  | HART | 448 | mmWC
60HBK10CT401 |  | TP | BEFORE FRONT PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 449 | --
60HBK30CT401 |  | TP | BEFORE FRONT PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 450 | --
60HBK10CT402 |  | TP | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 451 | --
60HBK30CT402 |  | TP | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 452 | --
60HLB10CT013 |  | TT | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 268 | °C
60HLB10CT014 |  | TT | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 269 | °C
60HBK10CT002 |  | TYPE-R TC | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1800 | °C | -- | -- | -- |  | P | 0 |  | - | 455 | --
60HBK30CT002 |  | TYPE-R TC | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1800 | °C | -- | -- | -- |  | P | 0 |  | - | 456 | --
60HLB10CT019/020 |  | TT | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 270 | °C
60HLB10CT015 |  | TT | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 271 | °C
60HLB10CT016 |  | TT | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 272 | °C
60HLB10CT021/022 |  | TT | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 273 | °C
60HBK10CT403 |  | TP | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 461 | --
60HBK30CT403 |  | TP | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 462 | --
60HBK10CP402 |  | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 463 | --
60HBK30CP402 |  | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 464 | --
60HLB10CT017 |  | TT | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 274 | °C
60HLB10CT018 |  | TT | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 275 | °C
60HBK10CT003 |  | TYPE-R TC | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1600 | °C | -- | -- | -- |  | P | 0 |  | - | 467 | --
60HBK30CT003 |  | TYPE-R TC | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1600 | °C | -- | -- | -- |  | P | 0 |  | - | 468 | --
60HLB10CT023/024 |  | TT | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 276 | °C
60HLB20CT001 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 287 | °C
60HBK10CP401 |  | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 471 | --
60HBK30CP401 |  | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 472 | --
60HBK10CT404 |  | TP | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 473 | --
60HBK30CT404 |  | TP | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 474 | --
60HLB20CT002 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 288 | °C
60HLB20CT003 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 289 | °C
60HBK10CT004 |  | TYPE-R TC | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1500 | °C | -- | -- | -- |  | P | 0 |  | - | 477 | --
60HBK30CT004 |  | TYPE-R TC | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1500 | °C | -- | -- | -- |  | P | 0 |  | - | 478 | --
60HLB20CT004 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 290 | °C
60HLB20CT005 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 291 | °C
60HBK10CP403 |  | PP | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 481 | --
60HBK30CP403 |  | PP | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 482 | --
60HBK10CT405 |  | TP | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 483 | --
60HBK30CT405 |  | TP | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 484 | --
60HLB20CT006 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 292 | °C
60HLB20CT007 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 293 | °C
60HBK10CT005 |  | TYPE-R TC | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1200 | °C | -- | -- | -- |  | P | 0 |  | - | 487 | --
60HBK30CT005 |  | TYPE-R TC | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 1200 | °C | -- | -- | -- |  | P | 0 |  | - | 488 | --
60HLB20CT008 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 294 | °C
60HLB20CT009 |  | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 295 | °C
60HBK10CP404 |  | PP | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 491 | --
60HBK30CP404 |  | PP | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 492 | --
60HBK10CT406 |  | TP | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 493 | --
60HBK30CT406 |  | TP | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 494 | --
60HLB20CT010 |  | TT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 301 | °C
60HLB20CT011 |  | TT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 302 | °C
60HBK10CT006 |  | TYPE-K TC | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 700 | °C | -- | -- | -- |  | P | 0 |  | - | 497 | --
60HBK30CT006 |  | TYPE-K TC | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 700 | °C | -- | -- | -- |  | P | 0 |  | - | 498 | --
60HLB20CT012 |  | TT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 303 | °C
60HLB20CT025 |  | TT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 311 | °C
60HBK10CP405 |  | PP | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 501 | --
60HBK30CP405 |  | PP | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 502 | --
60HBK10CT407 |  | TP | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 503 | --
60HBK30CT407 |  | TP | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 504 | --
60HLB20CT026 |  | TT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 312 | °C
60HLB20CT027 |  | TT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 313 | °C
60HBK10CT007 |  | TYPE-K TC | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 700 | °C | -- | -- | -- |  | P | 0 |  | - | 507 | --
60HBK30CT007 |  | TYPE-K TC | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- |  | 0 to 700 | °C | -- | -- | -- |  | P | 0 |  | - | 508 | --
60HLB20CT013 |  | TT | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 326 | °C
60HLB20CT014 |  | TT | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 327 | °C
60HBK10CP406 |  | PP | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 511 | --
60HBK30CP406 |  | PP | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 512 | --
60HLB20CT019/020 |  | TT | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 328 | °C
60HLB20CT015 |  | TT | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 329 | °C
60HNA01CT001 |  | TYPE-K TC | ECON OUTLET HOPPER-1 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 515 | --
60HLB20CT016 |  | TT | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 330 | °C
60HLB20CT021/022 |  | TT | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 331 | °C
60HLB20CT017 |  | TT | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 332 | °C
60HNA01CT002 |  | TYPE-K TC | ECON OUTLET HOPPER-2 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 519 | --
60HLB20CT018 |  | TT | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 333 | °C
60HLB20CT023/024 |  | TT | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 334 | °C
60HLA12CT001 |  | TT | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 336 | --
60HNA02CT001 |  | TYPE-K TC | ECON OUTLET HOPPER-3 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 523 | --
60HLA22CT001 |  | TT | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 344 | --
60HLA13CT001 |  | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 359 | --
60HLA13CT002 |  | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 360 | --
60HNA02CT002 |  | TYPE-K TC | ECON OUTLET HOPPER-4 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 527 | --
60HLA13CT003 |  | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 361 | --
60HNA10CP401 |  | PP | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 529 | --
60HLA13CT004 |  | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 362 | --
60HNA10CT001 |  | TYPE-K TC | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 531 | --
60HBK30CP009 |  | PT | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 496 | --
60HNA10CT401 |  | TP | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 533 | --
60HLA23CT001 |  | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 372 | --
60HLA23CT002 |  | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 373 | --
60HLA23CT003 |  | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 374 | --
60HNA10CQ401-407 |  | AP | ECON OUTLET FLUE GAS ANALYSER POCKET | FLUE GAS | 7 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 537 | --
60HNA20CP401 |  | PP | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 538 | --
60HLA23CT004 |  | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 75 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 375 | --
60HNA20CT001 |  | TYPE-K TC | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 540 | --
60HBK10CP010 |  | PT | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 505 | --
60HNA20CT401 |  | TP | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 542 | --
60HLA13CP002 |  | PDT | APH "A" COLD TO HOT SA DIFF. PRESS. | SA | 1 |  | 279 / 199 | 395 / 295 | mmWC | 30 / 331 | 55 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 377 | --
60HLA23CP002 |  | PDT | APH "B" COLD TO HOT SA DIFF. PRESS. | SA | 1 |  | 279 / 199 | 395 / 295 | mmWC | 30 / 331 | 55 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 378 | --
60HBK30CP010 |  | PT | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 506 | --
60HNA20CQ401-407 |  | AP | ECON OUTLET FLUE GAS ANALYSER POCKET | FLUE GAS | 7 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 546 | --
60HNA10CP001 |  | PT | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 530 | --
60HLA14CT001 |  | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 389 | --
60HNA10CT002 |  | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-1 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 549 | --
60HLA14CT002 |  | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 390 | --
60HLA14CT003 |  | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 391 | --
60HLA14CT004 |  | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 392 | --
60HNA10CT003 |  | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-2 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 553 | --
60HNA20CP001 |  | PT | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 539 | --
60HNA31CP001 |  | PT | AH-A FLUE GAS INLET PRESS | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 573 | --
60HLA24CT001 |  | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 403 | --
60HNA10CT004 |  | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-3 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 557 | --
60HLA24CT002 |  | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 404 | --
60HLA24CT003 |  | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 405 | --
60HLA24CT004 |  | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 406 | --
60HNA20CT002 |  | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-4 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 561 | --
60HNA41CP001 |  | PT | AH-B FLUE GAS INLET PRESS | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 588 | --
60HNA32CP001 |  | PT | AH-A FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -500 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 656 | --
60HLA15CF001 |  | FT | HOT SA "A" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- |  | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 0 | Refer FE characteristics | HART | 410 | --
60HNA20CT003 |  | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-5 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 565 | --
60HLA15CF002 |  | FT | HOT SA "A" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- |  | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 0 | Refer FE characteristics | HART | 411 | --
60HLA25CF001 |  | FT | HOT SA "B" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- |  | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 0 | Refer FE characteristics | HART | 413 | --
60HLA25CF002 |  | FT | HOT SA "B" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- |  | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 0 | Refer FE characteristics | HART | 414 | --
60HNA20CT004 |  | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-6 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 600 | °C | -- | -- | -- | -- | T | 0 |  | - | 569 | --
60HLA15CT001 |  | TT | HOT SA FROM APH "A" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | HART | 417 | --
60HLA15CT002 |  | TT | HOT SA FROM APH "A" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | HART | 418 | --
60HLA25CT001 |  | TT | HOT SA FROM APH "B" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | HART | 422 | --
60HLA25CT002 |  | TT | HOT SA FROM APH "B" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- |  | 0 to 500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | HART | 423 | --
60HNA31CT001 |  | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 574 | --
60HNA31CT002 |  | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 575 | --
60HNA31CT003 |  | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 576 | --
60HNA31CT004 |  | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 577 | --
60HNA42CP001 |  | PT | AH-B FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -500 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 669 | --
60HNC10CP001 |  | PT | ID FAN "A" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -600 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 739 | --
60HNC10CP004 |  | PT | ID FAN "A" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 744 | --
60HNC20CP001 |  | PT | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -600 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 749 | --
60HNA31CP401 |  | PP | AH-A FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 582 | --
60HNA31CT401 |  | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 583 | --
60HNA31CT402 |  | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 584 | --
60HNA31CT403 |  | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 585 | --
60HNA31CT404 |  | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 586 | --
60HNA31CT405 |  | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 587 | --
60HNC20CP004 |  | PT | ID FAN "B" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 754 | --
60HNA41CT001 |  | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 589 | --
60HNA41CT002 |  | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 590 | --
60HNA41CT003 |  | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 591 | --
60HNA41CT004 |  | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- |  | 0 to 600 | °C | -- | -- | -- |  | P | 0 |  | - | 592 | --
60HBK10CT001 |  | TT | FURNACE TEMP PROBE (LEFT SIDE) | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,N | >593 |  | 0 to 1900 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | HART | 438 | °C
60HBK30CT001 |  | TT | FURNACE TEMP PROBE (RIGHT SIDE) | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,N | >593 |  | 0 to 1900 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | HART | 439 | °C
60HFE01CP001 |  | PT | PA FAN "A" INLET AIR PRESS | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 2 | --
60HFE01CP004 |  | PT | PA FAN "A" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 7 | --
60HNA41CP401 |  | PP | AH-B FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 597 | --
60HNA41CT401 |  | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 598 | --
60HNA41CT402 |  | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 599 | --
60HNA41CT403 |  | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 600 | --
60HNA41CT404 |  | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 601 | --
60HNA41CT405 |  | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 602 | --
60HFE05CP001 |  | PT | PA FAN "B" INLET AIR PRESS | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 9 | --
60HFE05CP004 |  | PT | PA FAN "B" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 14 | --
60HBK10CT002 |  | TT | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1800 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 457 | --
60HBK30CT002 |  | TT | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1800 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 458 | --
60HBK10CQ001 |  | AT | BEFORE REAR PLATEN SH FLUE GAS OXYGEN | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 459 | --
60HBK30CQ001 |  | AT | BEFORE REAR PLATEN SH FLUE GAS OXYGEN | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 460 | --
60HFE02CP001 |  | PT | APH "A" INLET COLD PA PRESS | PA | 1 | 3450 x 3450 | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 163 | --
60HFE06CP001 |  | PT | APH "B" INLET COLD PA PRESS | PA | 1 | 3450 x 3450 | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 169 | --
60HBK10CT003 |  | TT | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 469 | --
60HBK30CT003 |  | TT | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 470 | --
60HFE03CP002 |  | PT | APH "A" HOT PA PRESS | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 183 | --
60HFE07CP002 |  | PT | APH "B" HOT PA PRESS | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 197 | --
60HBK10CT004 |  | TT | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 479 | --
60HBK30CT004 |  | TT | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1500 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 480 | --
60HLB10CP001 |  | PT | FD FAN "A" INLET AIR PRESS | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 206 | --
60HLB10CP004 |  | PT | FD FAN "A" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 211 | --
60HBK10CT005 |  | TT | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 489 | --
60HBK30CT005 |  | TT | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 1200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 490 | --
60HLB20CP001 |  | PT | FD FAN "B" INLET AIR PRESS | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- |  | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 213 | --
60HLB20CP004 |  | PT | FD FAN "B" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | HART | 218 | --
60HBK10CT006 |  | TT | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 700 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 499 | --
60HBK30CT006 |  | TT | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 700 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 500 | --
60HLA13CP001 |  | PT | APH "A" INLET COLD SA PRESS | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 363 | --
60HLA23CP001 |  | PT | APH "B" INLET COLD SA PRESS | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 376 | --
60HBK10CT007 |  | TT | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 700 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 509 | --
60HBK30CT007 |  | TT | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 700 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 510 | --
60HLD10CT001 |  | TYPE-K TC | AH-A ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 629 | --
60HNA01CT001 |  | TT | ECON OUTLET HOPPER-1 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 516 | --
60HLD10CT002 |  | TYPE-K TC | AH-A ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 631 | --
60HNA01CT002 |  | TT | ECON OUTLET HOPPER-2 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 520 | --
60HLD10CT003 |  | TYPE-K TC | AH-A ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 633 | --
60HNA02CT001 |  | TT | ECON OUTLET HOPPER-3 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 524 | --
60HLD10CT004 |  | TYPE-K TC | AH-A FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 635 | --
60HNA02CT002 |  | TT | ECON OUTLET HOPPER-4 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 528 | --
60HLD10CT005 |  | TYPE-K TC | AH-A FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 637 | --
60HLA14CP002 |  | PT | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 380 | --
60HLD10CT006 |  | TYPE-K TC | AH-A FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 639 | --
60HNA10CT001 |  | TT | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 532 | --
60HLD20CT001 |  | TYPE-K TC | AH-B ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 641 | --
60HNA10CQ001 |  | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 534 | --
60HLD20CT002 |  | TYPE-K TC | AH-B ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 643 | --
60HNA10CQ002 |  | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 535 | --
60HLD20CT003 |  | TYPE-K TC | AH-B ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 645 | --
60HNA10CQ003 |  | AT | ECON OUTLET FLUE GAS CO | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | <100 | -- | ppm | -- | -- | D/I,C | -- |  | 0 to 500 | ppm | -- | -- | -- | -- | P | 0 |  | - | 536 | --
60HLD20CT004 |  | TYPE-K TC | AH-B FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 647 | --
60HLA24CP002 |  | PT | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 394 | --
60HLD20CT005 |  | TYPE-K TC | AH-B FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 649 | --
60HNA20CT001 |  | TT | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 541 | --
60HLD20CT006 |  | TYPE-K TC | AH-B FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 300 | °C | -- | -- | -- | -- | T | 0 |  | - | 651 | --
60HNA20CQ001 |  | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 543 | --
60HNA20CQ002 |  | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 544 | --
60HNA20CQ003 |  | AT | ECON OUTLET FLUE GAS CO | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | <100 | -- | ppm | -- | -- | D/I,C | -- |  | 0 to 500 | ppm | -- | -- | -- | -- | P | 0 |  | - | 545 | --
60HNA32CQ401-407 |  | AP | AH-A HOT FLUE GAS SAMPLE ANALYSER POCKET | FLUE GAS | 7 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 655 | --
60HNA10CT002 |  | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-1 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 550 | --
60HNA32CT401 |  | TP | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 657 | --
60HNA32CT001 |  | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 658 | --
60HNA32CT002 |  | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 659 | --
60HNA32CT003 |  | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 660 | --
60HNA32CT004 |  | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 661 | --
60HNA10CT003 |  | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-2 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 554 | --
60HNA10CT004 |  | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-3 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 558 | --
60HNA20CT002 |  | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-4 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 562 | --
60HNA20CT003 |  | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-5 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 566 | --
60HNA20CT004 |  | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-6 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 570 | --
60HLA20CP001 |  | PT | HOT SA CROSSOVER DUCT | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 407 | --
60HNA42CQ401-407 |  | AP | AH-B HOT FLUE GAS SAMPLE ANALYSER POCKET | FLUE GAS | 7 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 668 | --
60HLA20CP002 |  | PT | HOT SA CROSSOVER DUCT | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 408 | --
60HNA42CT401 |  | TP | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 670 | --
60HNA42CT001 |  | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 671 | --
60HNA42CT002 |  | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 672 | --
60HNA42CT003 |  | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 673 | --
60HNA42CT004 |  | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 674 | --
60HLA18CP002 |  | PT | WINDBOX PRESS (LEFT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 200 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 443 | --
60HNA31CT001 |  | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 578 | --
60HNA31CT002 |  | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 579 | --
60HNA31CT003 |  | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 580 | --
60HNA31CT004 |  | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 581 | --
60HLA28CP002 |  | PT | WINDBOX PRESS (RIGHT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 200 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 444 | --
60HNA70CP401 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 681 | --
60HNA70CT401 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 682 | --
60HNA70CP402 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 683 | --
60HNA70CT402 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 684 | --
60HNA70CP403 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 685 | --
60HNA70CT403 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 686 | --
60HNA70CP404 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 687 | --
60HNA70CT404 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 688 | --
60HNA70CP405 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 689 | --
60HNA70CT405 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 690 | --
60HNA70CP406 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 691 | --
60HNA70CT406 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 692 | --
60HNA70CP407 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 693 | --
60HNA70CT407 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 694 | --
60HNA70CP408 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 695 | --
60HNA70CT408 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 696 | --
60HNA70CP409 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 697 | --
60HNA70CT409 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 698 | --
60HNA70CP410 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 699 | --
60HNA70CT410 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 700 | --
60HNA70CP411 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 701 | --
60HNA70CT411 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 702 | --
60HNA70CP412 |  | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 703 | --
60HNA70CT412 |  | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 704 | --
60HNC01CT401 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 705 | --
60HNC01CP401 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 706 | --
60HNC01CT402 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 707 | --
60HNC01CP402 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 708 | --
60HNC01CT403 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 709 | --
60HNC01CP403 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 710 | --
60HNC01CT404 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 711 | --
60HNC01CP404 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 712 | --
60HNC01CT405 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 713 | --
60HNC01CP405 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 714 | --
60HNC01CT406 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 715 | --
60HNC01CP406 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 716 | --
60HNC01CT407 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 717 | --
60HNC01CP407 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 718 | --
60HNC01CT408 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 719 | --
60HNC01CP408 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 720 | --
60HNC01CT409 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 721 | --
60HNC01CP409 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 722 | --
60HNC01CT410 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 723 | --
60HNC01CP410 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 724 | --
60HNC01CT411 |  | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 725 | --
60HNC01CP411 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 726 | --
60HNC01CT412 |  | TP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 727 | --
60HNC01CP412 |  | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 728 | --
60HNC01CQ001 |  | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- |  | -- | -- | -- | -- | -- | -- | R | 0 |  | - | 729 | --
60HNC01CQ002 |  | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- |  | -- | -- | -- | -- | -- | -- | R | 0 |  | - | 730 | --
60HNC01CQ003 |  | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- |  | -- | -- | -- | -- | -- | -- | R | 0 |  | - | 731 | --
60HNC01CQ004 |  | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- |  | -- | -- | -- | -- | -- | -- | R | 0 |  | - | 732 | --
60HNC01CQ005 |  | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- |  | -- | -- | -- | -- | -- | -- | R | 0 |  | - | 733 | --
60HNC01CQ006 |  | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- |  | -- | -- | -- | -- | -- | -- | R | 0 |  | - | 734 | --
60HNC11CP501 |  | PI | ID FAN "A" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 735 | --
60HNC11CT401 |  | TP | ID FAN "A" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 736 | --
60HNA41CT001 |  | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 593 | --
60HNC11CP401 |  | PP | ID FAN "A" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 738 | --
60HNA41CT002 |  | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 594 | --
60HNC10CT031 |  | PT-100 | ID FAN "A" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 740 | --
60HNA41CT003 |  | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 595 | --
60HNA41CT004 |  | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 600 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 596 | --
60HNA31CP002 |  | PDT | AH-A FLUE GAS DIFF. PRESS | FLUE GAS | 1 |  | -150 / -251 | -202 / -332 | mmWC | 355 / 131 | 400 / 150 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 603 | --
60HNA41CP002 |  | PDT | AH-B FLUE GAS DIFF. PRESS | FLUE GAS | 1 |  | -150 / -251 | -202 / -332 | mmWC | 355 / 131 | 400 / 150 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 |  | PROFIBUS | 604 | --
60HNC21CP501 |  | PI | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 745 | --
60HNC21CT401 |  | TP | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 746 | --
60HLD10CT001 |  | TT | AH-A ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 630 | --
60HNC21CP401 |  | PP | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 748 | --
60HLD10CT002 |  | TT | AH-A ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 632 | --
60HNC20CT031 |  | PT-100 | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 750 | --
60HLD10CT003 |  | TT | AH-A ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 634 | --
60HLD10CT004 |  | TT | AH-A FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 636 | --
60HLD20CT001 |  | TT | AH-B ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 642 | --
60HLD20CT002 |  | TT | AH-B ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 644 | --
60HNC10CY101 |  | VT | ID FAN "A" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 755 | --
60HNC10CT001 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 756 | --
60HNC10CT002 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 757 | --
60HNC10CT003 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 758 | --
60HNC10CT004 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 759 | --
60HNC10CT005 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 760 | --
60HNC10CT006 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 761 | --
60HNC10CT007 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 762 | --
60HNC10CT008 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 763 | --
60HNC10CT009 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 764 | --
60HNC10CT010 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 765 | --
60HNC10CT011 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 766 | --
60HNC10CT012 |  | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 767 | --
60HLD20CT003 |  | TT | AH-B ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 646 | --
60HLD20CT004 |  | TT | AH-B FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 300 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 648 | --
60HNA32CQ001 |  | AT | AH-A FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 653 | --
60HNA32CQ002 |  | AT | AH-A FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 654 | --
60HFE03CP001 |  | PT | SEAL AIR FAN PRESS - APH "A" HOT PA ISOL GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 184
60HNA32CT001 |  | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 662 | --
60HNA32CT002 |  | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 663 | --
60HNA32CT003 |  | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 664 | --
60HNA32CT004 |  | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 665 | --
60HNA42CQ001 |  | AT | AH-B FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 666 | --
60HNA42CQ002 |  | AT | AH-B FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 667 | --
60HFE07CP001 |  | PT | SEAL AIR FAN PRESS - APH "B" HOT PA ISOL GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 198
60HNC10CT033 |  | TE | ID FAN "A" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- |  | ** | ** | -- | -- | -- | -- | R | 0 | ** BY BHEL RANIPET/EDN | - | 780 | --
60HNA42CT001 |  | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 675 | --
60HNC10CT032 |  | TE | ID FAN "A" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- |  | ** | ** | -- | -- | -- | -- | R | 0 | ** BY BHEL RANIPET/EDN | - | 782 | --
60HNA42CT002 |  | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 676 | --
60HNC10CY005 |  | VT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 784 | mm/s
60HNC10CY006 |  | VT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 785 | mm/s
60HNC10CT028 |  | PT-100 | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 786 | --
60HNC10CT029 |  | PT-100 | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 787 | --
60HNC10CT030 |  | PT-100 | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 788 | --
60HNA42CT003 |  | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 677 | --
60HNA42CT004 |  | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 678 | --
60HNC11CQ001 |  | AT | ID FAN "A" COLD FLUE GAS INLET O2 | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 737 | --
60HNC10CY004 |  | VT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 792 | mm/s
60HNC10CY003 |  | VT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 793 | mm/s
60HNC10CY002 |  | VT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 794 | mm/s
60HNC10CY001 |  | VT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 795 | mm/s
60HNC10CT025 |  | PT-100 | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 796 | --
60HNC10CT026 |  | PT-100 | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 797 | --
60HNC10CT027 |  | PT-100 | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 798 | --
60HLA14CP001 |  | PT | SEAL AIR FAN PRESS - APH "A" SA O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 379
60HNC10CT031 |  | TT | ID FAN "A" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART | 741 | --
60HNC10CP002 |  | PDT | ID FAN "A" DP ACROSS SUCTION & IMPELLER | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 742 | --
60HNC10CT013 |  | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 802 | --
60HNC10CT014 |  | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 803 | --
60HNC10CT015 |  | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 804 | --
60HNC10CT016 |  | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 805 | --
60HNC10CT017 |  | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 806 | --
60HNC10CT018 |  | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 807 | --
60HNC10CT019 |  | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 808 | --
60HNC10CT020 |  | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 809 | --
60HNC10CT021 |  | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 810 | --
60HNC10CT022 |  | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 811 | --
60HNC10CT023 |  | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 812 | --
60HNC10CT024 |  | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 813 | --
60HNC10CP003 |  | PDT | ID FAN "A" STALL DETECTION PROBE | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 |  | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 743 | mmWC
60HLA24CP001 |  | PT | SEAL AIR FAN PRESS - APH "B" SA O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 393
60HNC21CQ001 |  | AT | ID FAN "B" COLD FLUE GAS INLET O2 | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- |  | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 747 | --
60HNA15CP001 |  | PT | SEAL AIR FAN PRESS AT AH INLET (SCR BYPASS) ISOLATION GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 571
60HNC20CT031 |  | TT | ID FAN "B" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART | 751 | --
60HNC20CP002 |  | PDT | ID FAN "B" DP ACROSS SUCTION & IMPELLER | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I | -- |  | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 752 | --
60HNC20CP003 |  | PDT | ID FAN "B" STALL DETECTION PROBE | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 |  | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 0 | # - TP details from Ranipet | HART | 753 | mmWC
60HNA25CP001 |  | PT | SEAL AIR FAN PRESS AT AH INLET (SCR BYPASS) ISOLATION GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 572
60HNC10CT001 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 768 | °C
60HNC20CY101 |  | VT | ID FAN "B" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 823 | --
60HNC20CT001 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 824 | --
60HNC20CT002 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 825 | --
60HNC20CT003 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 826 | --
60HNC20CT004 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 827 | --
60HNC20CT005 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 828 | --
60HNC20CT006 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 829 | --
60HNC20CT007 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 830 | --
60HNC20CT008 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 831 | --
60HNC20CT009 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 832 | --
60HNC20CT010 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 833 | --
60HNC20CT011 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 834 | --
60HNC20CT012 |  | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | R | 0 |  | - | 835 | --
60HNC10CT002 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 769 | °C
60HNC10CT003 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 770 | °C
60HNC10CT004 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 771 | °C
60HNC10CT005 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 772 | °C
60HNC10CT006 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 773 | °C
60HNC10CT007 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 774 | °C
60HNC10CT008 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 775 | °C
60HNC10CT009 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 776 | °C
60HNC10CT010 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 777 | °C
60HNC10CT011 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 778 | °C
60HNC10CT012 |  | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 779 | °C
60HNC10CT028 |  | TT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 789 | °C
60HNC20CT033 |  | TE | ID FAN "B" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- |  | ** | ** | -- | -- | -- | -- | R | 0 | ** BY BHEL RANIPET/EDN | - | 848 | --
60HNC10CT029 |  | TT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 790 | °C
60HNC20CT032 |  | TE | ID FAN "B" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- |  | ** | ** | -- | -- | -- | -- | R | 0 | ** BY BHEL RANIPET/EDN | - | 850 | --
60HNC10CT030 |  | TT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 791 | °C
60HNC20CY005 |  | VT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 852 | mm/s
60HNC20CY006 |  | VT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 853 | mm/s
60HNC20CT028 |  | PT-100 | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 854 | --
60HNC20CT029 |  | PT-100 | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 855 | --
60HNC20CT030 |  | PT-100 | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 856 | --
60HNC10CT025 |  | TT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 799 | °C
60HNC10CT026 |  | TT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 800 | °C
60HNC10CT027 |  | TT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 801 | °C
60HNC20CY004 |  | VT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 860 | mm/s
60HNC20CY003 |  | VT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 861 | mm/s
60HNC20CY002 |  | VT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 862 | mm/s
60HNC20CY001 |  | VT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 |  |  | mm/s | -- | -- | -- | -- | E | 0 |  | - | 863 | mm/s
60HNC20CT025 |  | PT-100 | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 864 | --
60HNC20CT026 |  | PT-100 | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 865 | --
60HNC20CT027 |  | PT-100 | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 866 | --
60HNC10CT013 |  | TT | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 814 | °C
60HNC10CT014 |  | TT | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 815 | °C
60HNC10CT019/020 |  | TT | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 816 | °C
60HNC20CT013 |  | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 870 | --
60HNC20CT014 |  | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 871 | --
60HNC20CT015 |  | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 872 | --
60HNC20CT016 |  | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 873 | --
60HNC20CT017 |  | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 874 | --
60HNC20CT018 |  | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 875 | --
60HNC20CT019 |  | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 876 | --
60HNC20CT020 |  | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 877 | --
60HNC20CT021 |  | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 878 | --
60HNC20CT022 |  | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 879 | --
60HNC20CT023 |  | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 880 | --
60HNC20CT024 |  | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- |  | 0 to 150 | °C | -- | -- | -- | -- | IS | 0 | T = ACTUAL RUNNING TEMP. OBSERVED. | - | 881 | --
60HNC10CT015 |  | TT | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 817 | °C
60HNC10CT016 |  | TT | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 818 | °C
60HNC10CT021/022 |  | TT | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 819 | °C
60HNC10CT017 |  | TT | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 820 | °C
60HNC10CT018 |  | TT | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 821 | °C
60HNC10CT023/024 |  | TT | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 822 | °C
60HNC20CT001 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 836 | °C
60HNC20CT002 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 837 | °C
60HNC20CT003 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 838 | °C
60HNC20CT004 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 839 | °C
60HNC20CT005 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 840 | °C
60HNC12CP501 |  | PI | ID FAN "A" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 893 | --
60HNC12CP401 |  | PP | ID FAN "A" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 894 | --
60HNC12CQ401 |  | AP | ID FAN "A" COLD FLUE GAS OUTLET ANALYSER POCKET | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 895 | --
60HNC12CT401 |  | TP | ID FAN "A" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 896 | --
60HNC12CT001 |  | PT-100 | ID FAN "A" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 897 | --
60HNC20CT006 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 841 | °C
60HNC20CT007 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 842 | °C
60HNC20CT008 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 843 | °C
60HNC22CP501 |  | PI | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- |  |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 1 |  | - | 901 | --
60HNC22CP401 |  | PP | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 902 | --
60HNC22CQ401 |  | AP | ID FAN "B" COLD FLUE GAS OUTLET ANALYSER POCKET | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 903 | --
60HNC22CT401 |  | TP | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- |  | -- | -- | -- | -- | -- | -- | -- | 0 |  | - | 904 | --
60HNC22CT001 |  | PT-100 | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- |  | 0 to 200 | °C | -- | -- | -- |  | P | 0 |  | - | 905 | --
60HNC20CT009 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 844 | °C
60HNC20CT010 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 845 | °C
60HNC20CT011 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 846 | °C
60HNC20CT012 |  | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS | 847 | °C
60HNC20CT028 |  | TT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 857 | °C
60HNC20CT029 |  | TT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 858 | °C
60HNC20CT030 |  | TT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 859 | °C
60HNC20CT025 |  | TT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 867 | °C
60HNC20CT026 |  | TT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 868 | °C
60HNC20CT027 |  | TT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 869 | °C
60HNC20CT013 |  | TT | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 882 | °C
60HNC20CT014 |  | TT | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 883 | °C
60HLA51CF001 |  | FT | LSOFA CORNER-1 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 918 | mmWC
60HLA52CF001 |  | FT | HSOFA CORNER-4 (FRONT WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 919 | mmWC
60HLA61CF001 |  | FT | LSOFA CORNER-2 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 920 | mmWC
60HLA62CF001 |  | FT | HSOFA CORNER-1 (LEFT WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 921 | mmWC
60HLA71CF001 |  | FT | LSOFA CORNER-3 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 922 | mmWC
60HLA72CF001 |  | FT | HSOFA CORNER-2 (REAR WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 923 | mmWC
60HLA81CF001 |  | FT | LSOFA CORNER-4 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 924 | mmWC
60HLA82CF001 |  | FT | HSOFA CORNER-3 (RIGHT WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  |  | 0-20 | mmWC |  | t/h | -- | -- | E | 0 | Flow element (Multi port Pitot tube) by Trichy | HART | 925 | mmWC
60HHL95CP106 |  | PS | HSOFA-C PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 926 | kg/cm²
60HHL95CP105 |  | PS | HSOFA-B PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 927 | kg/cm²
60HHL95CP104 |  | PS | HSOFA-A PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 928 | kg/cm²
60HHL95CP103 |  | PS | LSOFA-C PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 929 | kg/cm²
60HHL95CP102 |  | PS | LSOFA-B PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 930 | kg/cm²
60HHL95CP101 |  | PS | LSOFA-A PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 931 | kg/cm²
60HHL91CP104 |  | PS | EL CCOFA-A SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 932 | kg/cm²
60HHL91CP103 |  | PS | EL JJ SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 933 | kg/cm²
60HHL91CP102 |  | PS | EL J SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 934 | kg/cm²
60HHL91CP101 |  | PS | EL HJJ SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 935 | kg/cm²
60HHL81CP103 |  | PS | EL HJ SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 936 | kg/cm²
60HHL81CP102 |  | PS | EL H SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 937 | kg/cm²
60HHL81CP101 |  | PS | EL GHH SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 938 | kg/cm²
60HHL71CP103 |  | PS | EL GH SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 939 | kg/cm²
60HHL71CP102 |  | PS | EL G SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 940 | kg/cm²
60HHL71CP101 |  | PS | EL FGG SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 941 | kg/cm²
60HHL61CP103 |  | PS | EL FG SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 942 | kg/cm²
60HHL61CP102 |  | PS | EL F SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 943 | kg/cm²
60HHL61CP101 |  | PS | EL EFF SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 944 | kg/cm²
60HHL51CP103 |  | PS | EL EF SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 945 | kg/cm²
60HHL51CP102 |  | PS | EL E SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 946 | kg/cm²
60HHL51CP101 |  | PS | EL DEE SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 947 | kg/cm²
60HHL41CP103 |  | PS | EL DE SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 948 | kg/cm²
60HHL41CP102 |  | PS | EL D SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 949 | kg/cm²
60HHL41CP101 |  | PS | EL CDD SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 950 | kg/cm²
60HHL31CP103 |  | PS | EL CD SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 951 | kg/cm²
60HHL31CP102 |  | PS | EL C SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 952 | kg/cm²
60HHL31CP101 |  | PS | EL BCC SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 953 | kg/cm²
60HHL21CP103 |  | PS | EL BC SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 954 | kg/cm²
60HHL21CP102 |  | PS | EL B SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 955 | kg/cm²
60HHL21CP101 |  | PS | EL ABB SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 956 | kg/cm²
60HHL11CP103 |  | PS | EL AB SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 957 | kg/cm²
60HHL11CP102 |  | PS | EL A SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 958 | kg/cm²
60HHL11CP101 |  | PS | EL AA SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 959 | kg/cm²
60HHL11CP104 |  | PS | EL AAA SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 |  | -- | -- | -- | -- | -- | -- | E | 0 |  | - | 960 | kg/cm²
60HHL95AA106 |  | I/P | HSOFA-C POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 961 | --
60HHL95AA105 |  | I/P | HSOFA-B POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 962 | --
60HHL95AA104 |  | I/P | HSOFA-A POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 963 | --
60HHL95AA103 |  | I/P | LSOFA-C POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 964 | --
60HHL95AA102 |  | I/P | LSOFA-B POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 965 | --
60HHL95AA101 |  | I/P | LSOFA-A POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 966 | --
60HHL91AA104 |  | I/P | EL CCOFA-A SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 967 | --
60HHL91AA103 |  | I/P | EL JJ SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 968 | --
60HHL91AA102 |  | I/P | EL J SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 969 | --
60HHL91AA101 |  | I/P | EL HJJ SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 970 | --
60HHL81AA103 |  | I/P | EL HJ SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 971 | --
60HHL81AA102 |  | I/P | EL H SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 972 | --
60HHL81AA101 |  | I/P | EL GHH SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 973 | --
60HHL71AA103 |  | I/P | EL GH SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 974 | --
60HHL71AA102 |  | I/P | EL G SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 975 | --
60HHL71AA101 |  | I/P | EL FGG SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 976 | --
60HHL61AA103 |  | I/P | EL FG SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 977 | --
60HHL61AA102 |  | I/P | EL F SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 978 | --
60HHL61AA101 |  | I/P | EL EFF SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 979 | --
60HHL51AA103 |  | I/P | EL EF SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 980 | --
60HHL51AA102 |  | I/P | EL E SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 981 | --
60HHL51AA101 |  | I/P | EL DEE SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 982 | --
60HHL41AA103 |  | I/P | EL DE SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 983 | --
60HHL41AA102 |  | I/P | EL D SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 984 | --
60HHL41AA101 |  | I/P | EL CDD SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 985 | --
60HHL31AA103 |  | I/P | EL CD SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 986 | --
60HHL31AA102 |  | I/P | EL C SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 987 | --
60HHL31AA101 |  | I/P | EL BCC SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 988 | --
60HHL21AA103 |  | I/P | EL BC SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 989 | --
60HHL21AA102 |  | I/P | EL B SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 990 | --
60HHL21AA101 |  | I/P | EL ABB SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 991 | --
60HHL11AA103 |  | I/P | EL AB SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 992 | --
60HHL11AA102 |  | I/P | EL A SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 993 | --
60HHL11AA101 |  | I/P | EL AA SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 994 | --
60HHL11AA104 |  | I/P | EL AAA SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- |  | 4-20 | mA | 3-15 | psi | -- | -- | E | 0 |  | - | 995 | --
60HNC20CT019/020 |  | TT | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 884 | °C
60HNC20CT015 |  | TT | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 885 | °C
60HNC20CT016 |  | TT | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 886 | °C
60HNC20CT021/022 |  | TT | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 887 | °C
60HNC20CT017 |  | TT | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 888 | °C
60HNC20CT018 |  | TT | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 889 | °C
60HNC20CT023/024 |  | TT | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 |  | 0 to 150 | °C | -- | -- | -- | -- | E | 0 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS | 890 | °C
60HNC12CP001 |  | PT | SEAL AIR FAN PRESS - ID FAN-A O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 891
60HNC22CP001 |  | PT | SEAL AIR FAN PRESS - ID FAN -B O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 892
60HNC12CT001 |  | TT | ID FAN "A" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 898 | --
60HNC22CT001 |  | TT | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- |  | 0 to 200 | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 906 | --
60HNC31CP001 |  | PT | SEAL AIR FAN PRESS - METHANOL ISLAND I/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 0 |  |  | 909
60HNC30CF001 |  | AT | FLUE GAS FLOW METER AT STACK | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | -- | -- | -- | D/I | -- |  | -- | -- | -- | -- | -- | -- | P | 0 |  | - | 910 | --
60HNC30CQ001 |  | AT | FLUE GAS TO STACK CO2 | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | % by dry volume | -- | -- | D/I | -- |  |  | % by dry volume | -- | -- | -- | -- | P | 0 |  | - | 911 | --
60HNC30CQ002 |  | AT | FLUE GAS TO STACK CO | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | <100 | -- | ppm | -- | -- | D/I | -- |  | 0 to 500 | ppm | -- | -- | -- | -- | P | 0 |  | - | 912 | --
60HNC30CQ003 |  | AT | FLUE GAS TO STACK NOX | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | <146 | -- | ppm | -- | -- | D/I | -- |  | 0 to 1000 | ppm | -- | -- | -- | -- | P | 0 |  | - | 913 | --
60HNC30CQ004 |  | AT | FLUE GAS TO STACK SOX | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | <35 | -- | ppm | -- | -- | D/I | -- |  | 0 to 1000 | ppm | -- | -- | -- | -- | P | 0 |  | - | 914 | --
60HNC30CQ005 |  | AT | FLUE GAS TO STACK OPACITY | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | ppm | -- | -- | D/I | -- |  |  | ppm | -- | -- | -- | -- | P | 0 |  | - | 915 | --
60HNC30CQ006 |  | AT | FLUE GAS TO STACK Hg | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | mg/Nm3 | -- | -- | D/I | -- |  |  | mg/Nm³ | -- | -- | -- | -- | P | 0 |  | - | 916 | --
60HNC10CG001 |  | APT | ID FAN - A ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- |  | 4-20 | mA | 0-100 | % | -- | -- | R | 0 |  | - | 1012 | --
60HNC20CG001 |  | APT | ID FAN - B ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- |  | 4-20 | mA | 0-100 | % | -- | -- | R | 0 |  | - | 1013 | --
60HLB10CG001 |  | APT | FD FAN - A ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- |  | 4-20 | mA | 0-100 | % | -- | -- | R | 0 |  | - | 1014 | --
60HBB01CT001 to 018 |  | TYPE-K TC | INSIDE PENT HOUSE TEMPERATURE MEASUREMENT | AIR / GAS | 18 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | -- | -- |  |  | °C | -- | -- | -- | -- | T | 0 | PROFIBUS REMOTE I/O. (MTM type) | - | 1018 | --
60HBB10CT001 to 007, 60HBB20CT001 to 006, 60HBB30CT001 to 007, 60HBB40CT001 to 005 |  | TYPE-K TC | INSULATION SKIN TEMPERATURE MEASUREMENT | INSULATION | 25 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | -- | -- |  |  | °C | -- | -- | -- | -- | T | 0 |  | - | 1019 | --
60HLB20CG001 |  | APT | FD FAN - B ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- |  | 4-20 | mA | 0-100 | % | -- | -- | R | 0 |  | - | 1015 | --
60HBB15CT001 to 005, 60HBB25CT001 to 005, 60HBB35CT001 to 005, 60HBB45CT001 to 005 |  | TYPE-K TC | AMBIENT TEMPERATURE MEASUREMENT | AMBIENT AIR | 20 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | -- | -- |  |  | °C | -- | -- | -- | -- | T | 0 |  | - | 1021 | --
60HBB10CT001 to 007, 60HBB20CT001 to 006, 60HBB30CT001 to 007, 60HBB40CT001 to 005 |  | TT | INSULATION SKIN TEMPERATURE MEASUREMENT | INSULATION | 25 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | D/I,A |  |  |  | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 1020 | °C
60HBB15CT001 to 005, 60HBB25CT001 to 005, 60HBB35CT001 to 005, 60HBB45CT001 to 005 |  | TT | AMBIENT TEMPERATURE MEASUREMENT | AMBIENT AIR | 20 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | D/I,A |  |  |  | °C | -- | -- | -- | -- | P | 0 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS | 1022 | °C