## Sheet1
KKS TAG | DESCRIPTION | SNSR TYPE | PROFIBUS/CONVENTIONAL | MEDIUM | OPRTG PRESS | OPRTG TEMP | RANGE | RANGE UNIT | UNIT OF PRESS | UNIT OF TEMP | DRWG TITLE | REV NUMBER | INST REMARKS
LBA01CP511 | MS PRESS AT SH O/L-L | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CP512 | MS PRESS AT SH O/L-L | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT011 | MS TEMP AT SH O/L-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT011 | MS TEMP AT SH O/L-L | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT012 | MS TEMP AT SH O/L-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT012 | MS TEMP AT SH O/L-L | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT013 | MS TEMP AT SH O/L-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT013 | MS TEMP AT SH O/L-L | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT014 | MS TEMP-L BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT014 | MS TEMP-L BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT015 | MS TEMP-L BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT015 | MS TEMP-L BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA01CT511 | MS TEMP AT SH O/L-L | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CP511 | MS PRESS AT SH O/L-R | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CP512 | MS PRESS AT SH O/L-R | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT011 | MS TEMP AT SH O/L-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT011 | MS TEMP AT SH O/L-R | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT012 | MS TEMP AT SH O/L-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT012 | MS TEMP AT SH O/L-R | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT013 | MS TEMP AT SH O/L-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT013 | MS TEMP AT SH O/L-R | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT014 | MS TEMP-R BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT014 | MS TEMP-R BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT015 | MS TEMP-R BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT015 | MS TEMP-R BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA02CT511 | MS TEMP AT SH O/L-R | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CP011 | MS PRESS BEF HPBP-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CP012 | MS PRESS BEF HPBP-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CP013 | MS PRESS BEF HPBP-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CP014 | MS PRESS BEF EQ LINE-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CP015 | MS PRESS BEF EQ LINE-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CP016 | MS PRESS BEF EQ LINE-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CP511 | MS PRESS BEF HPBP-L | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT011 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT011 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT012 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT012 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT013 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT013 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT014 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT014 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA05CT511 | MS TEMP BEF HPBP-L | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CP011 | MS PRESS BEF HPBP-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CP012 | MS PRESS BEF HPBP-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CP013 | MS PRESS BEF HPBP-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CP014 | MS PRESS BEF EQ LINE-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CP015 | MS PRESS BEF EQ LINE-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CP016 | MS PRESS BEF EQ LINE-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CP511 | MS PRESS BEF HPBP-R | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT012 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT012 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT013 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT013 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT014 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT014 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT015 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT015 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA06CT511 | MS TEMP BEF HPBP-R | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA10CP011 | MS EQ LINE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA10CP012 | MS EQ LINE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA10CP013 | MS EQ LINE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA11CT008 | MS MTL TEMP BEF HPT-L | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA12CT008 | MS MTL TEMP BEF HPT-R | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT011 | MS Pipe Skin Temp Measurement-1 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT011 | MS Pipe Skin Temp Measurement-1 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT012 | MS Pipe Skin Temp Measurement-2 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT012 | MS Pipe Skin Temp Measurement-2 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT013 | MS Pipe Skin Temp Measurement-3 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT013 | MS Pipe Skin Temp Measurement-3 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT014 | MS Pipe Skin Temp Measurement-4 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT014 | MS Pipe Skin Temp Measurement-4 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT015 | MS Pipe Skin Temp Measurement-5 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT015 | MS Pipe Skin Temp Measurement-5 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT016 | MS Pipe Skin Temp Measurement-6 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT016 | MS Pipe Skin Temp Measurement-6 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT017 | MS Pipe Skin Temp Measurement-7 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA18CT017 | MS Pipe Skin Temp Measurement-7 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT011 | MS Pipe Skin Temp Measurement-8 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA19CT011 | MS Pipe Skin Temp Measurement-8 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT012 | MS Pipe Skin Temp Measurement-9 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA19CT012 | MS Pipe Skin Temp Measurement-9 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT013 | MS Pipe Skin Temp Measurement-10 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA19CT013 | MS Pipe Skin Temp Measurement-10 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT014 | MS Pipe Skin Temp Measurement-11 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA19CT014 | MS Pipe Skin Temp Measurement-11 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT015 | MS Pipe Skin Temp Measurement-12 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA19CT015 | MS Pipe Skin Temp Measurement-12 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT016 | MS Pipe Skin Temp Measurement-13 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA19CT016 | MS Pipe Skin Temp Measurement-13 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT017 | MS Pipe Skin Temp Measurement-14 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBA19CT017 | MS Pipe Skin Temp Measurement-14 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT010 | MS Pipe Stress Measurement | Stress Meas (Cr-Al) | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA18CT010 | MS Pipe Stress Measurement | TT-S | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT010 | MS Pipe Stress Measurement | Stress Meas (Cr-Al) | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBA19CT010 | MS Pipe Stress Measurement | TT-S | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CP011 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CP012 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CP013 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CP014 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CP511 | HRH STM PRESS AT RH O/L-L | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CP512 | HRH STM PRESS AT RH O/L-L | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT011 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT011 | HRH STM TEMP AT RH O/L-L | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT012 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT012 | HRH STM TEMP AT RH O/L-L | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT013 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT013 | HRH STM TEMP AT RH O/L-L | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT014 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT014 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT015 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT015 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT016 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT016 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT017 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT017 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT018 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT018 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB01CT511 | HRH STM TEMP AT RH O/L-L | TI | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CP011 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CP012 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CP013 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CP014 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CP511 | HRH STM PRESS AT RH O/L-R | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CP512 | HRH STM PRESS AT RH O/L-R | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT011 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT011 | HRH STM TEMP AT RH O/L-R | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT012 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT012 | HRH STM TEMP AT RH O/L-R | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT013 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT013 | HRH STM TEMP AT RH O/L-R | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT014 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT014 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT015 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT015 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT016 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT016 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT017 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT017 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT018 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT018 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB02CT511 | HRH STM TEMP AT RH O/L-R | TI | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB11CT006 | IP TURB I/L-R MTL TEMP | Cr-Al | --- | METAL | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB11CT006 | IP TURB I/L-R MTL TEMP | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB12CT006 | IP TURB I/L-L MTL TEMP | Cr-Al | --- | METAL | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB12CT006 | IP TURB I/L-L MTL TEMP | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB18CT011 | HRH Pipe Skin Temp Measurement-1 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB18CT011 | HRH Pipe Skin Temp Measurement-1 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB18CT012 | HRH Pipe Skin Temp Measurement-2 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB18CT012 | HRH Pipe Skin Temp Measurement-2 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB18CT013 | HRH Pipe Skin Temp Measurement-3 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB18CT013 | HRH Pipe Skin Temp Measurement-3 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB18CT014 | HRH Pipe Skin Temp Measurement-4 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB18CT014 | HRH Pipe Skin Temp Measurement-4 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB18CT015 | HRH Pipe Skin Temp Measurement-5 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB18CT015 | HRH Pipe Skin Temp Measurement-5 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB19CT011 | HRH Pipe Skin Temp Measurement-6 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB19CT011 | HRH Pipe Skin Temp Measurement-6 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB19CT012 | HRH Pipe Skin Temp Measurement-7 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB19CT012 | HRH Pipe Skin Temp Measurement-7 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB19CT013 | HRH Pipe Skin Temp Measurement-8 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB19CT013 | HRH Pipe Skin Temp Measurement-8 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB19CT014 | HRH Pipe Skin Temp Measurement-9 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB19CT014 | HRH Pipe Skin Temp Measurement-9 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBB19CT015 | HRH Pipe Skin Temp Measurement-10 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0 | Skin Temp
LBB19CT015 | HRH Pipe Skin Temp Measurement-10 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CP011 | CRH STM PRESS AT RH I/L-L | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CP511 | CRH STM PRESS AT RH I/L-L | PI | --- | STM | 66.18 | 372.2 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CT011 | CRH STM TEMP AT RH I/L-L | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CT011 | CRH STM TEMP AT RH I/L-L | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CT012 | CRH STM TEMP AT RH I/L-L | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CT012 | CRH STM TEMP AT RH I/L-L | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CT013 | CRH STM TEMP AT RH I/L-L | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CT013 | CRH STM TEMP AT RH I/L-L | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC01CT511 | CRH STM TEMP AT RH I/L-L | TI | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CP011 | CRH STM PRESS AT RH I/L-R | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CP511 | CRH STM PRESS AT RH I/L-R | PI | --- | STM | 66.18 | 372.2 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CT011 | CRH STM TEMP AT RH I/L-R | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CT011 | CRH STM TEMP AT RH I/L-R | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CT012 | CRH STM TEMP AT RH I/L-R | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CT012 | CRH STM TEMP AT RH I/L-R | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CT013 | CRH STM TEMP AT RH I/L-R | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CT013 | CRH STM TEMP AT RH I/L-R | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC02CT511 | CRH STM TEMP AT RH I/L-R | TI | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC05CP011 | DP ACRS RH I/L & O/L HDR-L | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC05CP012 | DP ACRS RH I/L & O/L HDR-L | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC05CP013 | DP ACRS RH I/L & O/L HDR-L | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC06CP011 | DP ACRS RH I/L & O/L HDR-R | DPT | PROFIBUS | STM | 66.18 | 372.2 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC06CP012 | DP ACRS RH I/L & O/L HDR-R | DPT | PROFIBUS | STM | 66.18 | 372.2 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC06CP013 | DP ACRS RH I/L & O/L HDR-R | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CL111 | CRH DRN POT LVL | LS-Cond | --- | STM | --- | --- | --- | --- | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CL112 | CRH DRN POT LVL | LS-Cond | --- | STM | --- | --- | --- | --- | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CP011 | CRH STM HDR PRESS AFT NRV | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CP012 | CRH STM HDR PRESS AFT NRV | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CP511 | CRH STM HDR PRESS AFT NRV | PI | --- | STM | 66.18 | 372.2 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT002 | CRH STM TEMP AT HPT EXHAUST | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT002 | CRH STM TEMP AT HPT EXHAUST | Cr-Al | --- | STM | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT003 | CRH STM TEMP AT HPT EXHAUST | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT003 | CRH STM TEMP AT HPT EXHAUST | Cr-Al | --- | STM | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT004 | CRH STM TEMP AT HPT EXHAUST | Cr-Al | --- | STM | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT004 | CRH STM TEMP AT HPT EXHAUST | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT011 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT011 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT012 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT012 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT013 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT013 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT014 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
LBC10CT014 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
MAA50CP004 | TURBINE 1ST STAGE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
MAA50CP005 | TURBINE 1ST STAGE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
MAA50CP006 | TURBINE 1ST STAGE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 0
| ECON INLET BOILER FW TEMP |  |  | WATER
| FEED WATER LINE DRAIN |  |  | METAL
| ECON INLET BOILER FW TEMP |  |  | WATER
| WARM UP THRU AUXILIARY WATER RETURN TEMP |  |  | WATER
| ECON DRAIN TEMP |  |  | METAL
| WARM UP THRU AUXILIARY WATER RETURN TEMP |  |  | WATER
| ECON OUTLET LINK |  |  | WATER
| WARM UP LINE TO BLR RECIRC SYS TEMP |  |  | WATER
| STARTUP SYSTEM MIXING PIECE |  |  | WATER
| ECON OUTLET LINK |  |  | WATER
| BWCP SUCTION LINE |  |  | WATER
| BOILER WATER CIRC PUMP |  |  | WATER
| BOILER WATER CIRC PUMP |  |  | WATER
| BOILER WATER CIRC PUMP |  |  | WATER
| BWCP COOLING WTR SUPPLY TEMP |  |  | WATER
| BWCP COOLING WTR SUPPLY TEMP |  |  | WATER
| BWCP COOLING WTR RETURN TEMP |  |  | WATER
| BWCP COOLING WTR RETURN TEMP |  |  | WATER
| ECON INLET BOILER FW FLOW |  |  | WATER
| ECON INLET BOILER FW FLOW |  |  | WATER
| ECON INLET BOILER FW FLOW |  |  | WATER
| ECON INLET BOILER FW PRESS |  |  | WATER
| ECON MIXING LINE |  |  | WATER
| ECON INLET BOILER FW TEMP |  |  | WATER
| ECON MIXING LINE |  |  | WATER
| ECON INLET BOILER FW TEMP |  |  | WATER
| FURN LWR FRONT & REAR INLET HDR DRAIN TEMP |  |  | METAL
| ECON DRAIN TEMP |  |  | METAL
| ECON INLET HEADER TEMP |  |  | METAL
| ECON OUTLET HEADER TEMP |  |  | METAL
| FURN INTER. LEFT SIDE HDR DRAIN TEMP. |  |  | METAL
| ECON OUTLET LINK |  |  | WATER
| FURN INTER. FRONT HDR DRAIN TEMP. |  |  | METAL
| ECON OUTLET LINK |  |  | WATER
| FURN INTER. REAR HDR DRAIN TEMP. |  |  | METAL
| ECON MIXING LINE |  |  | WATER
| FURN INTER.RIGHT SIDE HDR DRAIN TEMP. |  |  | METAL
| ECON MIXING LINE |  |  | WATER
| SEPARATOR STRG TANK "A" TEMP |  |  | WATER
| FURN LWR FRONT & REAR INLET HDR DRAIN TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | WATER
| FURN INTER. LEFT SIDE HDR DRAIN TEMP. |  |  | METAL
| WTR STORAGE TANK DOWNCOMER TEMP |  |  | WATER
| FURN INTER. FRONT HDR DRAIN TEMP. |  |  | METAL
| WARM UP THRU AUXILIARY WATER RETURN TEMP |  |  | WATER
| FURN INTER. REAR HDR DRAIN TEMP. |  |  | METAL
| WARM UP THRU AUXILIARY WATER RETURN TEMP |  |  | WATER
| FURN INTER.RIGHT SIDE HDR DRAIN TEMP. |  |  | METAL
| WATER SEPARATOR "A" OUTLET PRESS |  |  | STEAM
| WARM UP LINE TO BLR RECIRC SYS TEMP |  |  | WATER
| WATER SEPARATOR "A" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "A" OUTLET PRESS |  |  | STEAM
| BWCP SUCTION LINE |  |  | WATER
| WATER SEPARATOR "A" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "A" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "A" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "A" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "A" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "B" OUTLET PRESS |  |  | STEAM
| WATER SEPARATOR "A" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "B" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "B" OUTLET PRESS |  |  | STEAM
| WATER SEPARATOR "A" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "B" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "B" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "B" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "B" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "B" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "C" OUTLET PRESS |  |  | STEAM
| WATER SEPARATOR "B" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "C" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "C" OUTLET PRESS |  |  | STEAM
| WATER SEPARATOR "B" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "C" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "C" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "C" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "C" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "C" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "D" OUTLET PRESS |  |  | STEAM
| WATER SEPARATOR "C" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "D" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "D" OUTLET PRESS |  |  | STEAM
| WATER SEPARATOR "C" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "D" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "D" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "D" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "D" OUTLET TEMP |  |  | STEAM
| WATER SEPARATOR "D" OUTLET VENT TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "A" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "B" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "C" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| WATER SEPARATOR "D" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" LEVEL |  |  | WATER
| SEPARATOR STRG TANK "A" LEVEL |  |  | WATER
| SEPARATOR STRG TANK "A" LEVEL |  |  | WATER
| SEPARATOR STRG TANK "A" PRESS |  |  | WATER
| SEPARATOR STRG TANK "A" PRESS |  |  | WATER
| WATER SEPARATOR "D" OUTLET VENT TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | METAL
| SEPARATOR STRG TANK "A" TEMP |  |  | WATER
| SEPARATOR STRG TANK "B" LEVEL |  |  | WATER
| SEPARATOR STRG TANK "B" LEVEL |  |  | WATER
| SEPARATOR STRG TANK "B" LEVEL |  |  | WATER
| SEPARATOR STRG TANK "B" PRESS |  |  | WATER
| SEPARATOR STRG TANK "B" PRESS |  |  | WATER
| WATER SEPARATOR "D" OUTLET VENT TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | METAL
| SEPARATOR STRG TANK "B" TEMP |  |  | WATER
| SEPARATOR STRG TANK "A" DNCOMER LEVEL |  |  | WATER
| SEPARATOR STRG TANK "B" DNCOMER LEVEL |  |  | WATER
| SH FURN ROOF INLET HDR DRAIN TEMP |  |  | METAL
| WTR STORAGE TANK DOWNCOMER TEMP |  |  | WATER
| WTR STORAGE TANK DOWNCOMER PRESS |  |  | WATER
| BP LOWER FRONT HDR DRAIN TEMP |  |  | METAL
| SH FURN ROOF INLET HDR DRAIN TEMP |  |  | METAL
| BP LOWER REAR HDR DRAIN TEMP |  |  | METAL
| BP LOWER FRONT HDR DRAIN TEMP |  |  | METAL
| LINK TO SH FRONT PLATEN INLET HEADER TEMP |  |  | STEAM
| BP LOWER REAR HDR DRAIN TEMP |  |  | METAL
| LINK TO SH FRONT PLATEN INLET HEADER TEMP |  |  | STEAM
| LINK TO SH FRONT PLATEN INLET HEADER TEMP |  |  | STEAM
| SH / DSH STAGE-I "A" INLET TEMP |  |  | STEAM
| LINK TO SH FRONT PLATEN INLET HEADER TEMP |  |  | STEAM
| SH / DSH STAGE-I "A" SPRAY WATER PRESS |  |  | WATER
| SH / DSH STAGE-I "A" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "A" SPRAY WATER TEMP |  |  | WATER
| SH / DSH STAGE-I "A" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-I "A" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-I "B" SPRAY WATER PRESS |  |  | WATER
| SH / DSH STAGE-I"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "B" SPRAY WATER TEMP |  |  | WATER
| SH / DSH STAGE-I "B" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-I "B" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-I"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "A" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "A" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "A" OUTLET PRESS |  |  | STEAM
| SH / DSH STAGE-I"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I "B" OUTLET PRESS |  |  | STEAM
| SH / DSH STAGE-II "A" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "A" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-I"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "A" SPRAY WATER PRESS |  |  | WATER
| SH / DSH STAGE-II"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "A" SPRAY WATER TEMP |  |  | WATER
| SH / DSH STAGE-II "A" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-II "A" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-II "B" SPRAY WATER PRESS |  |  | WATER
| SH / DSH STAGE-II"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "B" SPRAY WATER TEMP |  |  | WATER
| SH / DSH STAGE-II "B" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-II "B" SPRAY WATER FLOW |  |  | WATER
| SH / DSH STAGE-II "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "A" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "A" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-II"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-II"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II "B" INLET TEMP |  |  | STEAM
| SH / DSH STAGE-II"A" OUTLET PRESS |  |  | STEAM
| SH / DSH STAGE-II"B" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II"A" OUTLET TEMP |  |  | STEAM
| RH / DSH "A" INLET |  |  | STEAM
| SH / DSH STAGE-II"A" OUTLET TEMP |  |  | STEAM
| RH / DSH "A" INLET |  |  | STEAM
| SH / DSH STAGE-II"A" OUTLET TEMP |  |  | STEAM
| SH / DSH STAGE-II"B" OUTLET PRESS |  |  | STEAM
| RH / DSH "A" OUTLET |  |  | STEAM
| SH / DSH STAGE-II"B" OUTLET TEMP |  |  | STEAM
| RH / DSH "A" OUTLET |  |  | STEAM
| SH / DSH STAGE-II"B" OUTLET TEMP |  |  | STEAM
| RH / DSH "A" OUTLET |  |  | STEAM
| SH / DSH STAGE-II"B" OUTLET TEMP |  |  | STEAM
| RH / DSH "B" INLET |  |  | STEAM
| SH FINISH OUTLET VENT-1 TEMP |  |  | METAL
| RH / DSH "B" INLET |  |  | STEAM
| SH FINISH OUTLET VENT-2 TEMP |  |  | METAL
| RH / DSH "B" OUTLET |  |  | STEAM
| SH FINISH OUTLET VENT-3 TEMP |  |  | METAL
| RH / DSH "B" OUTLET |  |  | STEAM
| SH FINISH OUTLET VENT-4 TEMP |  |  | METAL
| RH / DSH "B" OUTLET |  |  | STEAM
| SH ERV LEFT-VENT TEMP |  |  | METAL
| FEED WATER LINE DRAIN |  |  | METAL
| SH ERV RIGHT-VENT TEMP |  |  | METAL
| RH / DSH "A" SPRAY WATER |  |  | WATER
| SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| RH / DSH "B" SPRAY WATER |  |  | WATER
| SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| SH / DSH STAGE-I "A" SPRAY WATER TEMP |  |  | WATER
| SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| SH / DSH STAGE-I "B" SPRAY WATER TEMP |  |  | WATER
| SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| SH / DSH STAGE-II "A" SPRAY WATER TEMP |  |  | WATER
| RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| SH / DSH STAGE-II "B" SPRAY WATER TEMP |  |  | WATER
| RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| SH FINISH OUTLET VENT-1 TEMP |  |  | METAL
| RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| SH FINISH OUTLET VENT-2 TEMP |  |  | METAL
| RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| RH / DSH "A" SPRAY WATER PRESS |  |  | WATER
| SH ERV LEFT-VENT TEMP |  |  | METAL
| RH / DSH "A" SPRAY WATER |  |  | WATER
| RH / DSH "A" SPRAY WATER |  |  | WATER
| RH / DSH "A" SPRAY WATER |  |  | WATER
| RH / DSH "B" SPRAY WATER PRESS |  |  | WATER
| SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| RH / DSH "B" SPRAY WATER |  |  | WATER
| RH / DSH "B" SPRAY WATER |  |  | WATER
| RH / DSH "B" SPRAY WATER |  |  | WATER
| SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| RH / DSH "A" INLET |  |  | STEAM
| SH FINISH OUTLET VENT-3 TEMP |  |  | METAL
| RH / DSH "A" INLET |  |  | STEAM
| SH FINISH OUTLET VENT-4 TEMP |  |  | METAL
| RH / DSH "B" INLET |  |  | STEAM
| SH ERV RIGHT-VENT TEMP |  |  | METAL
| RH / DSH "B" INLET |  |  | STEAM
| RH / DSH "A" OUTLET |  |  | STEAM
| SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| RH / DSH "A" OUTLET |  |  | STEAM
| SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP |  |  | METAL
| RH / DSH "A" OUTLET |  |  | STEAM
| RH OUTLET LEFT- VENT TEMP |  |  | METAL
| RH / DSH "A" OUTLET |  |  | STEAM
| RH / DSH "B" OUTLET |  |  | STEAM
| RH ERV LEFT- VENT TEMP |  |  | METAL
| RH / DSH "B" OUTLET |  |  | STEAM
| RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| RH / DSH "B" OUTLET |  |  | STEAM
| RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| RH / DSH "B" OUTLET |  |  | STEAM
| RH OUTLET RIGHT- VENT TEMP |  |  | METAL
| RH OUTLET LEFT- VENT TEMP |  |  | METAL
| RH ERV RIGHT- VENT TEMP |  |  | METAL
| RH ERV LEFT- VENT TEMP |  |  | METAL
| RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| RH ERV RIGHT- VENT TEMP |  |  | METAL
| RH OUTLET RIGHT- VENT TEMP |  |  | METAL
| RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| RH ERV RIGHT- VENT TEMP |  |  | METAL
| RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| RH ERV RIGHT- VENT TEMP |  |  | METAL
| RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP |  |  | METAL
| RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP |  |  | METAL
| PA FAN "A" INLET AIR TEMP |  |  | PA
| PA FAN "B" INLET AIR TEMP |  |  | PA
| AH-A FG O/L DUCT HOPPER-2 TEMP |  |  | METAL
| AH-A FG O/L DUCT HOPPER-3 TEMP |  |  | METAL
| AH-B FG O/L DUCT HOPPER-2 TEMP |  |  | METAL
| AH-B FG O/L DUCT HOPPER-3 TEMP |  |  | METAL
| ID FAN "A" COLD FLUE GAS OUTLET O2 |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS OUTLET CO2 |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS OUTLET O2 |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS OUTLET CO2 |  |  | FLUE GAS
| FLUE GAS TO STACK O2 |  |  | FLUE GAS
| PA FAN "A" OUTLET AIR TEMP |  |  | PA
| PA FAN "B" OUTLET AIR TEMP |  |  | PA
| APH "A" HOT PA TEMP |  |  | PA
| APH "A" HOT PA TEMP |  |  | PA
| APH "A" HOT PA TEMP |  |  | PA
| APH "A" HOT PA TEMP |  |  | PA
| APH "B" HOT PA TEMP |  |  | PA
| APH "B" HOT PA TEMP |  |  | PA
| APH "B" HOT PA TEMP |  |  | PA
| APH "B" HOT PA TEMP |  |  | PA
| FURNACE PRESS |  |  | FLUE GAS
| PA FAN "A" INLET AIR TEMP |  |  | PA
| PA FAN "A" DP ACROSS SUCTION & IMPELLER |  |  | PA
| PA FAN "A" STALL DETECTION PROBE |  |  | PA
| FURNACE PRESS |  |  | FLUE GAS
| FURNACE PRESS |  |  | FLUE GAS
| PA FAN "B" INLET AIR TEMP |  |  | PA
| PA FAN "B" DP ACROSS SUCTION & IMPELLER |  |  | PA
| FD FAN "A" INLET AIR TEMP |  |  | SA
| PA FAN "B" STALL DETECTION PROBE |  |  | PA
| FURNACE PRESS |  |  | FLUE GAS
| FD FAN "B" INLET AIR TEMP |  |  | SA
| PA FAN "A" OUTLET AIR TEMP |  |  | PA
| FD FAN "A" OUTLET AIR TEMP |  |  | SA
| PA FAN "B" OUTLET AIR TEMP |  |  | PA
| FD FAN "B" OUTLET AIR TEMP |  |  | SA
| FURNACE PRESS |  |  | FLUE GAS
| APH "A" INLET COLD SA TEMP |  |  | SA
| APH "A" INLET COLD SA TEMP |  |  | SA
| APH "A" INLET COLD SA TEMP |  |  | SA
| APH "A" INLET COLD SA TEMP |  |  | SA
| APH "A" COLD TO HOT PA DIFF. PRESS. |  |  | PA
| BEFORE REAR PLATEN SH FLUE GAS PRESS |  |  | FLUE GAS
| APH "B" COLD TO HOT PA DIFF. PRESS. |  |  | PA
| APH "A" HOT PA TEMP |  |  | PA
| APH "A" HOT PA TEMP |  |  | PA
| APH "B" INLET COLD SA TEMP |  |  | SA
| APH "B" INLET COLD SA TEMP |  |  | SA
| APH "B" INLET COLD SA TEMP |  |  | SA
| APH "B" INLET COLD SA TEMP |  |  | SA
| APH "A" HOT PA TEMP |  |  | PA
| APH "A" HOT PA TEMP |  |  | PA
| BEFORE REAR PLATEN SH FLUE GAS PRESS |  |  | FLUE GAS
| FINISH RH INLET FLUE GAS PRESS |  |  | FLUE GAS
| APH "B" HOT PA TEMP |  |  | PA
| APH "B" HOT PA TEMP |  |  | PA
| APH "B" HOT PA TEMP |  |  | PA
| APH "B" HOT PA TEMP |  |  | PA
| FINISH RH INLET FLUE GAS PRESS |  |  | FLUE GAS
| APH "A" OUTLET HOT SA |  |  | SA
| APH "A" OUTLET HOT SA |  |  | SA
| APH "A" OUTLET HOT SA |  |  | SA
| APH "A" OUTLET HOT SA |  |  | SA
| FINISH SH INLET FLUE GAS PRESS |  |  | FLUE GAS
| FURN TO HOT PA DUCT |  |  | FLUE GAS/HOT PY. AIR
| FURN TO HOT PA DUCT |  |  | FLUE GAS/HOT PY. AIR
| FURN TO HOT PA DUCT |  |  | FLUE GAS/HOT PY. AIR
| FINISH SH INLET FLUE GAS PRESS |  |  | FLUE GAS
| FD FAN "A" INLET AIR TEMP |  |  | SA
| APH "B" OUTLET HOT SA |  |  | SA
| APH "B" OUTLET HOT SA |  |  | SA
| APH "B" OUTLET HOT SA |  |  | SA
| APH "B" OUTLET HOT SA |  |  | SA
| FD FAN "A" DP ACROSS SUCTION & IMPELLER |  |  | SA
| FD FAN "A" STALL DETECTION PROBE |  |  | SA
| LTRH INLET FLUE GAS PRESS |  |  | FLUE GAS
| LTRH INLET FLUE GAS PRESS |  |  | FLUE GAS
| FD FAN "B" INLET AIR TEMP |  |  | SA
| FD FAN "B" DP ACROSS SUCTION & IMPELLER |  |  | SA
| FD FAN "B" STALL DETECTION PROBE |  |  | SA
| ECON INLET FLUE GAS PRESS |  |  | FLUE GAS
| HOT SA FROM APH "A" |  |  | SA
| HOT SA FROM APH "A" |  |  | SA
| HOT SA FROM APH "B" |  |  | SA
| HOT SA FROM APH "B" |  |  | SA
| BEFORE REAR PLATEN SH FLUE GAS TEMP |  |  | FLUE GAS
| BEFORE REAR PLATEN SH FLUE GAS TEMP |  |  | FLUE GAS
| FINISH RH INLET FLUE GAS TEMP |  |  | FLUE GAS
| FINISH RH INLET FLUE GAS TEMP |  |  | FLUE GAS
| FINISH SH INLET FLUE GAS TEMP |  |  | FLUE GAS
| FINISH SH INLET FLUE GAS TEMP |  |  | FLUE GAS
| LTRH INLET FLUE GAS TEMP |  |  | FLUE GAS
| LTRH INLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON INLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON INLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON INTERMEDIATE BANK FLUE GAS TEMP |  |  | FLUE GAS
| ECON INTERMEDIATE BANK FLUE GAS TEMP |  |  | FLUE GAS
| FD FAN "A" OUTLET AIR TEMP |  |  | SA
| FD FAN "B" OUTLET AIR TEMP |  |  | SA
| APH "A" INLET COLD SA TEMP |  |  | SA
| APH "A" INLET COLD SA TEMP |  |  | SA
| APH "A" INLET COLD SA TEMP |  |  | SA
| APH "A" INLET COLD SA TEMP |  |  | SA
| ECON OUTLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON INLET FLUE GAS PRESS |  |  | FLUE GAS
| APH "B" INLET COLD SA TEMP |  |  | SA
| APH "B" INLET COLD SA TEMP |  |  | SA
| APH "B" INLET COLD SA TEMP |  |  | SA
| APH "B" INLET COLD SA TEMP |  |  | SA
| ECON OUTLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON INTERMEDIATE BANK FLUE GAS PRESS |  |  | FLUE GAS
| APH "A" COLD TO HOT SA DIFF. PRESS. |  |  | SA
| APH "B" COLD TO HOT SA DIFF. PRESS. |  |  | SA
| ECON INTERMEDIATE BANK FLUE GAS PRESS |  |  | FLUE GAS
| ECON OUTLET FLUE GAS PRESS |  |  | FLUE GAS
| APH "A" OUTLET HOT SA |  |  | SA
| APH "A" OUTLET HOT SA |  |  | SA
| APH "A" OUTLET HOT SA |  |  | SA
| APH "A" OUTLET HOT SA |  |  | SA
| ECON OUTLET FLUE GAS PRESS |  |  | FLUE GAS
| AH-A FLUE GAS INLET PRESS |  |  | FLUE GAS
| APH "B" OUTLET HOT SA |  |  | SA
| APH "B" OUTLET HOT SA |  |  | SA
| APH "B" OUTLET HOT SA |  |  | SA
| APH "B" OUTLET HOT SA |  |  | SA
| AH-B FLUE GAS INLET PRESS |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET PRESS |  |  | FLUE GAS
| HOT SA "A" AIR |  |  | SA
| HOT SA "A" AIR |  |  | SA
| HOT SA "B" AIR |  |  | SA
| HOT SA "B" AIR |  |  | SA
| HOT SA FROM APH "A" |  |  | SA
| HOT SA FROM APH "A" |  |  | SA
| HOT SA FROM APH "B" |  |  | SA
| HOT SA FROM APH "B" |  |  | SA
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET PRESS |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS INLET PRESS |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS OUTLET PRESS |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS INLET PRESS |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS OUTLET PRESS |  |  | FLUE GAS
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| PA FAN "A" INLET AIR PRESS |  |  | PA
| PA FAN "A" OUTLET AIR PRESS |  |  | PA
| PA FAN "B" INLET AIR PRESS |  |  | PA
| PA FAN "B" OUTLET AIR PRESS |  |  | PA
| BEFORE REAR PLATEN SH FLUE GAS TEMP |  |  | FLUE GAS
| BEFORE REAR PLATEN SH FLUE GAS TEMP |  |  | FLUE GAS
| BEFORE REAR PLATEN SH FLUE GAS OXYGEN |  |  | FLUE GAS
| BEFORE REAR PLATEN SH FLUE GAS OXYGEN |  |  | FLUE GAS
| APH "A" INLET COLD PA PRESS |  |  | PA
| APH "B" INLET COLD PA PRESS |  |  | PA
| FINISH RH INLET FLUE GAS TEMP |  |  | FLUE GAS
| FINISH RH INLET FLUE GAS TEMP |  |  | FLUE GAS
| APH "A" HOT PA PRESS |  |  | PA
| APH "B" HOT PA PRESS |  |  | PA
| FINISH SH INLET FLUE GAS TEMP |  |  | FLUE GAS
| FINISH SH INLET FLUE GAS TEMP |  |  | FLUE GAS
| FD FAN "A" INLET AIR PRESS |  |  | SA
| FD FAN "A" OUTLET AIR PRESS |  |  | SA
| LTRH INLET FLUE GAS TEMP |  |  | FLUE GAS
| LTRH INLET FLUE GAS TEMP |  |  | FLUE GAS
| FD FAN "B" INLET AIR PRESS |  |  | SA
| FD FAN "B" OUTLET AIR PRESS |  |  | SA
| ECON INLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON INLET FLUE GAS TEMP |  |  | FLUE GAS
| APH "A" INLET COLD SA PRESS |  |  | SA
| APH "B" INLET COLD SA PRESS |  |  | SA
| ECON INTERMEDIATE BANK FLUE GAS TEMP |  |  | FLUE GAS
| ECON INTERMEDIATE BANK FLUE GAS TEMP |  |  | FLUE GAS
| ECON OUTLET HOPPER-1 TEMP |  |  | METAL
| ECON OUTLET HOPPER-2 TEMP |  |  | METAL
| ECON OUTLET HOPPER-3 TEMP |  |  | METAL
| ECON OUTLET HOPPER-4 TEMP |  |  | METAL
| APH "A" OUTLET HOT SA |  |  | SA
| ECON OUTLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON OUTLET FLUE GAS OXYGEN |  |  | FLUE GAS
| ECON OUTLET FLUE GAS OXYGEN |  |  | FLUE GAS
| ECON OUTLET FLUE GAS CO |  |  | FLUE GAS
| APH "B" OUTLET HOT SA |  |  | SA
| ECON OUTLET FLUE GAS TEMP |  |  | FLUE GAS
| ECON OUTLET FLUE GAS OXYGEN |  |  | FLUE GAS
| ECON OUTLET FLUE GAS OXYGEN |  |  | FLUE GAS
| ECON OUTLET FLUE GAS CO |  |  | FLUE GAS
| ECO OUTLET DUCT (SCR INLET) HOPPER-1 TEMP |  |  | METAL
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| ECO OUTLET DUCT (SCR INLET) HOPPER-2 TEMP |  |  | METAL
| ECO OUTLET DUCT (SCR INLET) HOPPER-3 TEMP |  |  | METAL
| ECO OUTLET DUCT (SCR INLET) HOPPER-4 TEMP |  |  | METAL
| ECO OUTLET DUCT (SCR INLET) HOPPER-5 TEMP |  |  | METAL
| ECO OUTLET DUCT (SCR INLET) HOPPER-6 TEMP |  |  | METAL
| HOT SA CROSSOVER DUCT |  |  | SA
| HOT SA CROSSOVER DUCT |  |  | SA
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| WINDBOX PRESS (LEFT SIDE) |  |  | SA
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS INLET TEMP |  |  | FLUE GAS
| WINDBOX PRESS (RIGHT SIDE) |  |  | SA
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS INLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS DIFF. PRESS |  |  | FLUE GAS
| AH-B FLUE GAS DIFF. PRESS |  |  | FLUE GAS
| AH-A ASH HOPPER-1 TEMP |  |  | METAL
| AH-A ASH HOPPER-2 TEMP |  |  | METAL
| ID FAN "B" COLD FLUE GAS INLET PRESS |  |  | FLUE GAS
| AH-A ASH HOPPER-3 TEMP |  |  | METAL
| AH-A FG O/L DUCT HOPPER-1 TEMP |  |  | METAL
| AH-B ASH HOPPER-1 TEMP |  |  | METAL
| AH-B ASH HOPPER-2 TEMP |  |  | METAL
| AH-B ASH HOPPER-3 TEMP |  |  | METAL
| AH-B FG O/L DUCT HOPPER-1 TEMP |  |  | METAL
| AH-A FLUE GAS OUTLET OXYGEN |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET OXYGEN |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-A FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET OXYGEN |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET OXYGEN |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| AH-B FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS INLET O2 |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS INLET TEMP |  |  | FLUE GAS
| ID FAN "A" DP ACROSS SUCTION & IMPELLER |  |  | FLUE GAS
| ID FAN "A" STALL DETECTION PROBE |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS INLET O2 |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS INLET TEMP |  |  | FLUE GAS
| ID FAN "B" DP ACROSS SUCTION & IMPELLER |  |  | FLUE GAS
| ID FAN "B" STALL DETECTION PROBE |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| ID FAN "A" COLD FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| ID FAN "B" COLD FLUE GAS OUTLET TEMP |  |  | FLUE GAS
| FLUE GAS FLOW METER AT STACK |  |  | FLUE GAS
| FLUE GAS TO STACK CO2 |  |  | FLUE GAS
| FLUE GAS TO STACK CO |  |  | FLUE GAS
| FLUE GAS TO STACK NOX |  |  | FLUE GAS
| FLUE GAS TO STACK SOX |  |  | FLUE GAS
| FLUE GAS TO STACK OPACITY |  |  | FLUE GAS
| FLUE GAS TO STACK Hg |  |  | FLUE GAS
| INSULATION SKIN TEMPERATURE MEASUREMENT |  |  | INSULATION
| AMBIENT TEMPERATURE MEASUREMENT |  |  | AMBIENT AIR