## Sheet1
KKS TAG | DESCRIPTION | SNSR TYPE | PROFIBUS/CONVENTIONAL | MEDIUM | OPRTG PRESS | OPRTG TEMP | RANGE | RANGE UNIT | UNIT OF PRESS | UNIT OF TEMP | DRWG TITLE | REV NUMBER | INST REMARKS
LBA01CP511 | MS PRESS AT SH O/L-L | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CP512 | MS PRESS AT SH O/L-L | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT011 | MS TEMP AT SH O/L-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT011 | MS TEMP AT SH O/L-L | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT012 | MS TEMP AT SH O/L-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT012 | MS TEMP AT SH O/L-L | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT013 | MS TEMP AT SH O/L-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT013 | MS TEMP AT SH O/L-L | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT014 | MS TEMP-L BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT014 | MS TEMP-L BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT015 | MS TEMP-L BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT015 | MS TEMP-L BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA01CT511 | MS TEMP AT SH O/L-L | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CP511 | MS PRESS AT SH O/L-R | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CP512 | MS PRESS AT SH O/L-R | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT011 | MS TEMP AT SH O/L-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT011 | MS TEMP AT SH O/L-R | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT012 | MS TEMP AT SH O/L-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT012 | MS TEMP AT SH O/L-R | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT013 | MS TEMP AT SH O/L-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT013 | MS TEMP AT SH O/L-R | TT-S | HART | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT014 | MS TEMP-R BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT014 | MS TEMP-R BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT015 | MS TEMP-R BEF APRDS | Cr-Al | --- | STM | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT015 | MS TEMP-R BEF APRDS | TT-S | PROFIBUS | --- | 270 | 600 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA02CT511 | MS TEMP AT SH O/L-R | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CP011 | MS PRESS BEF HPBP-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CP012 | MS PRESS BEF HPBP-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CP013 | MS PRESS BEF HPBP-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CP014 | MS PRESS BEF EQ LINE-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CP015 | MS PRESS BEF EQ LINE-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CP016 | MS PRESS BEF EQ LINE-L | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CP511 | MS PRESS BEF HPBP-L | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT011 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT011 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT012 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT012 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT013 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT013 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT014 | MS TEMP BEF HPBP-L | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT014 | MS TEMP BEF HPBP-L | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA05CT511 | MS TEMP BEF HPBP-L | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CP011 | MS PRESS BEF HPBP-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CP012 | MS PRESS BEF HPBP-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CP013 | MS PRESS BEF HPBP-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CP014 | MS PRESS BEF EQ LINE-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CP015 | MS PRESS BEF EQ LINE-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CP016 | MS PRESS BEF EQ LINE-R | PT | PROFIBUS | STM | 279 | 603 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CP511 | MS PRESS BEF HPBP-R | PI | --- | STM | 279 | 603 | 0-400 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT012 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT012 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT013 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT013 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT014 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT014 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT015 | MS TEMP BEF HPBP-R | Cr-Al | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT015 | MS TEMP BEF HPBP-R | TT-S | PROFIBUS | --- | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA06CT511 | MS TEMP BEF HPBP-R | TI | --- | STM | 279 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA10CP011 | MS EQ LINE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA10CP012 | MS EQ LINE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA10CP013 | MS EQ LINE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA11CT008 | MS MTL TEMP BEF HPT-L | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA12CT008 | MS MTL TEMP BEF HPT-R | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT011 | MS Pipe Skin Temp Measurement-1 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT011 | MS Pipe Skin Temp Measurement-1 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT012 | MS Pipe Skin Temp Measurement-2 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT012 | MS Pipe Skin Temp Measurement-2 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT013 | MS Pipe Skin Temp Measurement-3 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT013 | MS Pipe Skin Temp Measurement-3 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT014 | MS Pipe Skin Temp Measurement-4 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT014 | MS Pipe Skin Temp Measurement-4 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT015 | MS Pipe Skin Temp Measurement-5 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT015 | MS Pipe Skin Temp Measurement-5 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT016 | MS Pipe Skin Temp Measurement-6 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT016 | MS Pipe Skin Temp Measurement-6 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT017 | MS Pipe Skin Temp Measurement-7 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA18CT017 | MS Pipe Skin Temp Measurement-7 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT011 | MS Pipe Skin Temp Measurement-8 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA19CT011 | MS Pipe Skin Temp Measurement-8 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT012 | MS Pipe Skin Temp Measurement-9 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA19CT012 | MS Pipe Skin Temp Measurement-9 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT013 | MS Pipe Skin Temp Measurement-10 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA19CT013 | MS Pipe Skin Temp Measurement-10 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT014 | MS Pipe Skin Temp Measurement-11 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA19CT014 | MS Pipe Skin Temp Measurement-11 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT015 | MS Pipe Skin Temp Measurement-12 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA19CT015 | MS Pipe Skin Temp Measurement-12 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT016 | MS Pipe Skin Temp Measurement-13 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA19CT016 | MS Pipe Skin Temp Measurement-13 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT017 | MS Pipe Skin Temp Measurement-14 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBA19CT017 | MS Pipe Skin Temp Measurement-14 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT010 | MS Pipe Stress Measurement | Stress Meas (Cr-Al) | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA18CT010 | MS Pipe Stress Measurement | TT-S | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT010 | MS Pipe Stress Measurement | Stress Meas (Cr-Al) | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBA19CT010 | MS Pipe Stress Measurement | TT-S | --- | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CP011 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CP012 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CP013 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CP014 | HRH STM PRESS AT RH O/L-L | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CP511 | HRH STM PRESS AT RH O/L-L | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CP512 | HRH STM PRESS AT RH O/L-L | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT011 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT011 | HRH STM TEMP AT RH O/L-L | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT012 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT012 | HRH STM TEMP AT RH O/L-L | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT013 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT013 | HRH STM TEMP AT RH O/L-L | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT014 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT014 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT015 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT015 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT016 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT016 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT017 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT017 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT018 | HRH STM TEMP AT RH O/L-L | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT018 | HRH STM TEMP AT RH O/L-L | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB01CT511 | HRH STM TEMP AT RH O/L-L | TI | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CP011 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CP012 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CP013 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CP014 | HRH STM PRESS AT RH O/L-R | PT | PROFIBUS | STM | 63.36 | 603 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CP511 | HRH STM PRESS AT RH O/L-R | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CP512 | HRH STM PRESS AT RH O/L-R | PI | --- | STM | 63.36 | 603 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT011 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT011 | HRH STM TEMP AT RH O/L-R | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT012 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT012 | HRH STM TEMP AT RH O/L-R | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT013 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT013 | HRH STM TEMP AT RH O/L-R | TT-S | HART | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT014 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT014 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT015 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT015 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT016 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT016 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT017 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT017 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT018 | HRH STM TEMP AT RH O/L-R | Cr-Al | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT018 | HRH STM TEMP AT RH O/L-R | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB02CT511 | HRH STM TEMP AT RH O/L-R | TI | --- | STM | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB11CT006 | IP TURB I/L-R MTL TEMP | Cr-Al | --- | METAL | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB11CT006 | IP TURB I/L-R MTL TEMP | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB12CT006 | IP TURB I/L-L MTL TEMP | Cr-Al | --- | METAL | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB12CT006 | IP TURB I/L-L MTL TEMP | TT-S | PROFIBUS | --- | 63.36 | 603 | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB18CT011 | HRH Pipe Skin Temp Measurement-1 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB18CT011 | HRH Pipe Skin Temp Measurement-1 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB18CT012 | HRH Pipe Skin Temp Measurement-2 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB18CT012 | HRH Pipe Skin Temp Measurement-2 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB18CT013 | HRH Pipe Skin Temp Measurement-3 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB18CT013 | HRH Pipe Skin Temp Measurement-3 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB18CT014 | HRH Pipe Skin Temp Measurement-4 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB18CT014 | HRH Pipe Skin Temp Measurement-4 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB18CT015 | HRH Pipe Skin Temp Measurement-5 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB18CT015 | HRH Pipe Skin Temp Measurement-5 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB19CT011 | HRH Pipe Skin Temp Measurement-6 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB19CT011 | HRH Pipe Skin Temp Measurement-6 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB19CT012 | HRH Pipe Skin Temp Measurement-7 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB19CT012 | HRH Pipe Skin Temp Measurement-7 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB19CT013 | HRH Pipe Skin Temp Measurement-8 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB19CT013 | HRH Pipe Skin Temp Measurement-8 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB19CT014 | HRH Pipe Skin Temp Measurement-9 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB19CT014 | HRH Pipe Skin Temp Measurement-9 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBB19CT015 | HRH Pipe Skin Temp Measurement-10 | Cr-Al | --- | METAL | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00 | Skin Temp
LBB19CT015 | HRH Pipe Skin Temp Measurement-10 | TT-S | PROFIBUS | --- | --- | --- | 0-650 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CP011 | CRH STM PRESS AT RH I/L-L | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CP511 | CRH STM PRESS AT RH I/L-L | PI | --- | STM | 66.18 | 372.2 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CT011 | CRH STM TEMP AT RH I/L-L | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CT011 | CRH STM TEMP AT RH I/L-L | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CT012 | CRH STM TEMP AT RH I/L-L | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CT012 | CRH STM TEMP AT RH I/L-L | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CT013 | CRH STM TEMP AT RH I/L-L | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CT013 | CRH STM TEMP AT RH I/L-L | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC01CT511 | CRH STM TEMP AT RH I/L-L | TI | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CP011 | CRH STM PRESS AT RH I/L-R | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CP511 | CRH STM PRESS AT RH I/L-R | PI | --- | STM | 66.18 | 372.2 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CT011 | CRH STM TEMP AT RH I/L-R | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CT011 | CRH STM TEMP AT RH I/L-R | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CT012 | CRH STM TEMP AT RH I/L-R | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CT012 | CRH STM TEMP AT RH I/L-R | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CT013 | CRH STM TEMP AT RH I/L-R | Cr-Al | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CT013 | CRH STM TEMP AT RH I/L-R | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC02CT511 | CRH STM TEMP AT RH I/L-R | TI | --- | STM | 66.18 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC05CP011 | DP ACRS RH I/L & O/L HDR-L | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC05CP012 | DP ACRS RH I/L & O/L HDR-L | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC05CP013 | DP ACRS RH I/L & O/L HDR-L | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC06CP011 | DP ACRS RH I/L & O/L HDR-R | DPT | PROFIBUS | STM | 66.18 | 372.2 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC06CP012 | DP ACRS RH I/L & O/L HDR-R | DPT | PROFIBUS | STM | 66.18 | 372.2 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC06CP013 | DP ACRS RH I/L & O/L HDR-R | DPT | PROFIBUS | STM | 62.59 | 603 | 0-7 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CL111 | CRH DRN POT LVL | LS-Cond | --- | STM | --- | --- | --- | --- | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CL112 | CRH DRN POT LVL | LS-Cond | --- | STM | --- | --- | --- | --- | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CP011 | CRH STM HDR PRESS AFT NRV | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CP012 | CRH STM HDR PRESS AFT NRV | PT | PROFIBUS | STM | 66.18 | 372.2 | 0-80 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CP511 | CRH STM HDR PRESS AFT NRV | PI | --- | STM | 66.18 | 372.2 | 0-100 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT002 | CRH STM TEMP AT HPT EXHAUST | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT002 | CRH STM TEMP AT HPT EXHAUST | Cr-Al | --- | STM | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT003 | CRH STM TEMP AT HPT EXHAUST | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT003 | CRH STM TEMP AT HPT EXHAUST | Cr-Al | --- | STM | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT004 | CRH STM TEMP AT HPT EXHAUST | Cr-Al | --- | STM | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT004 | CRH STM TEMP AT HPT EXHAUST | TT-S | PROFIBUS | --- | 66.18 | 372.2 | 0-550 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT011 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT011 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT012 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT012 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT013 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT013 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT014 | CRH STM HDR TEMP AFT NRV | Cr-Al | --- | STM | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
LBC10CT014 | CRH STM HDR TEMP AFT NRV | TT-S | PROFIBUS | --- | 62.21 | 372.2 | 0-500 | DEG C | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
MAA50CP004 | TURBINE 1ST STAGE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
MAA50CP005 | TURBINE 1ST STAGE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00
MAA50CP006 | TURBINE 1ST STAGE PRESS | PT | HART | STM | 270 | 600 | 0-350 | kg/cm2 | kg/cm2 | DEG C | PID OF MS,CRH & HRH | 00