## MNC 2
LINE_ITEM | TAG_NUMBER | TYPE_OF_INST | DESCRIPTION | MEDIUM | QTY/BOILER | LINE_SIZE | OP_PRESS | MAX_PRESS | UNIT_OF_PRESS | OP_TEMP | MAX_TEMP | UNIT_OF_TEMP | OP_OTHERS | MAX_OTHERS | UNIT_OF_OTHERS | MAX_VELOCITY (m/sec) | INSULATION_THICKNESS (mm) | FUNCTION | SET POINT | Unit | RANGE_OF_PY_INST | UNIT_OF_PY_INST | RANGE _OF_SEC_INST | UNIT_OF_SEC_INST | CONTACT ACTION | INST_END_CONN | SCOPE | REVISION | REMARKS | TYPE OF PROTOCOL (HART/PROFIBUS)
1 | 60HFE01CP401 | PP | PA FAN "A" INLET AIR PRESS | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
513 | 60HNA01CL101 | LS | ECON OUTLET HOPPER-1 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
3 | 60HFE01CT031 | PT-100 | PA FAN "A" INLET AIR TEMP | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
514 | 60HNA01CL103 | LS | ECON OUTLET HOPPER-1 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
517 | 60HNA01CL102 | LS | ECON OUTLET HOPPER-2 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
518 | 60HNA01CL104 | LS | ECON OUTLET HOPPER-2 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
521 | 60HNA02CL101 | LS | ECON OUTLET HOPPER-3 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
8 | 60HFE05CP401 | PP | PA FAN "B" INLET AIR PRESS | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
522 | 60HNA02CL103 | LS | ECON OUTLET HOPPER-3 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
10 | 60HFE05CT031 | PT-100 | PA FAN "B" INLET AIR TEMP | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
525 | 60HNA02CL102 | LS | ECON OUTLET HOPPER-4 LSH | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
526 | 60HNA02CL104 | LS | ECON OUTLET HOPPER-4 LSL | FLY ASH | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
547 | 60HNA10CL101 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 1- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
548 | 60HNA10CL104 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 1- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
15 | 60HFE01CY101 | VT | PA FAN "A" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- | -- | -- | -- | -- | -- | -- | -- | E | 00 |  | -
16 | 60HFE01CT001 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
17 | 60HFE01CT002 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
18 | 60HFE01CT003 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
19 | 60HFE01CT004 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
20 | 60HFE01CT005 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
21 | 60HFE01CT006 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
22 | 60HFE01CT007 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
23 | 60HFE01CT008 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
24 | 60HFE01CT009 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
25 | 60HFE01CT010 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
26 | 60HFE01CT011 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
27 | 60HFE01CT012 | PT-100 | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
551 | 60HNA10CL102 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 2- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
552 | 60HNA10CL105 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 2- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
555 | 60HNA10CL103 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 3- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
556 | 60HNA10CL106 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 3- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
559 | 60HNA20CL101 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 4- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
560 | 60HNA20CL104 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 4- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
563 | 60HNA20CL102 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 5- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
564 | 60HNA20CL105 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 5- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
567 | 60HNA20CL103 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 6- LSH | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
568 | 60HNA20CL106 | LS | ECO OUTLET DUCT (SCR INLET) HOPPER 6- LSL | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
605 | 60HLD10CL101 | LS | AH-A ASH HOPPER-1 - LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
606 | 60HLD10CL102 | LS | AH-A ASH HOPPER-2- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
40 | 60HFE01CY005 | VT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
41 | 60HFE01CY006 | VT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
42 | 60HFE01CT028 | PT-100 | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
43 | 60HFE01CT029 | PT-100 | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
44 | 60HFE01CT030 | PT-100 | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
607 | 60HLD10CL103 | LS | AH-A ASH HOPPER-3- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
608 | 60HLD10CL104 | LS | AH-A FG O/L DUCT HOPPER-1 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
609 | 60HLD10CL105 | LS | AH-A FG O/L DUCT HOPPER-2 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
48 | 60HFE01CY004 | VT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
49 | 60HFE01CY003 | VT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
50 | 60HFE01CY002 | VT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
51 | 60HFE01CY001 | VT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
52 | 60HFE01CT025 | PT-100 | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
53 | 60HFE01CT026 | PT-100 | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
54 | 60HFE01CT027 | PT-100 | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
610 | 60HLD10CL106 | LS | AH-A FG O/L DUCT HOPPER-3 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
611 | 60HLD10CL107 | LS | AH-A ASH HOPPER-1 - LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
612 | 60HLD10CL108 | LS | AH-A ASH HOPPER-2- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
58 | 60HFE01CT013 | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
59 | 60HFE01CT014 | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
60 | 60HFE01CT015 | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
61 | 60HFE01CT016 | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
62 | 60HFE01CT017 | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
63 | 60HFE01CT018 | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
64 | 60HFE01CT019 | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
65 | 60HFE01CT020 | PT-100 | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
66 | 60HFE01CT021 | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
67 | 60HFE01CT022 | PT-100 | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
68 | 60HFE01CT023 | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
69 | 60HFE01CT024 | PT-100 | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
613 | 60HLD10CL109 | LS | AH-A ASH HOPPER-3- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
614 | 60HLD10CL110 | LS | AH-A FG O/L DUCT HOPPER-1 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
615 | 60HLD10CL111 | LS | AH-A FG O/L DUCT HOPPER-2 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
616 | 60HLD10CL112 | LS | AH-A FG O/L DUCT HOPPER-3 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
617 | 60HLD20CL101 | LS | AH-B ASH HOPPER-1 - LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
618 | 60HLD20CL102 | LS | AH-B ASH HOPPER-2- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
619 | 60HLD20CL103 | LS | AH-B ASH HOPPER-3- LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
620 | 60HLD20CL104 | LS | AH-B FG O/L DUCT HOPPER-1 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
621 | 60HLD20CL105 | LS | AH-B FG O/L DUCT HOPPER-2 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
79 | 60HFE05CY101 | VT | PA FAN "B" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- | -- | -- | -- | -- | -- | -- | -- | E | 00 |  | -
80 | 60HFE05CT001 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
81 | 60HFE05CT002 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
82 | 60HFE05CT003 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
83 | 60HFE05CT004 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
84 | 60HFE05CT005 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
85 | 60HFE05CT006 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
86 | 60HFE05CT007 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
87 | 60HFE05CT008 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
88 | 60HFE05CT009 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
89 | 60HFE05CT010 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
90 | 60HFE05CT011 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
91 | 60HFE05CT012 | PT-100 | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
622 | 60HLD20CL106 | LS | AH-B FG O/L DUCT HOPPER-3 LSH | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COI | -- | T | 00 | ** Vertical distance from top of hopper | -
623 | 60HLD20CL107 | LS | AH-B ASH HOPPER-1 - LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
624 | 60HLD20CL108 | LS | AH-B ASH HOPPER-2- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
625 | 60HLD20CL109 | LS | AH-B ASH HOPPER-3- LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
626 | 60HLD20CL110 | LS | AH-B FG O/L DUCT HOPPER-1 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
627 | 60HLD20CL111 | LS | AH-B FG O/L DUCT HOPPER-2 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
628 | 60HLD20CL112 | LS | AH-B FG O/L DUCT HOPPER-3 LSL | FLY ASH | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/A,N | ** Later | mm | -- | -- | -- | -- | COD | -- | T | 00 | ** Vertical distance from top of hopper | -
638 | 60HLD10CT005 | TT | AH-A FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
640 | 60HLD10CT006 | TT | AH-A FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
650 | 60HLD20CT005 | TT | AH-B FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
652 | 60HLD20CT006 | TT | AH-B FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
679 | 60HNA50CL001-008 | LT | DUCT ASH LEVEL MEASUREMENT - APH OUTLET (ESP INLET DUCT ASH LEVEL MEASUREMENT) | FLUE GAS | 8 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 13 | -- | D/I | -- | -- |  |  | 4 to 20 | mA | -- | -- | T | 01 |  | HART
104 | 60HFE05CY005 | VT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
105 | 60HFE05CY006 | VT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
106 | 60HFE05CT028 | PT-100 | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
107 | 60HFE05CT029 | PT-100 | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
108 | 60HFE05CT030 | PT-100 | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
680 | 60HNA10CL001, 60HNA20CL001 | LT | ECO OUTLET DUCT ASH LEVEL MEASUREMENT | FLUE GAS | 2 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 13 | -- | D/I | -- | -- |  |  | 4 to 20 | mA | -- | -- | T | 01 |  | HART
781 | 60HNC10CT033 | TT | ID FAN "A" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** | ** | ** | ** | -- | -- | -- | -- | E | 00 | ** BY BHEL RANIPET/EDN | PROFIBUS
783 | 60HNC10CT032 | TT | ID FAN "A" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** | ** | ** | ** | -- | -- | -- | -- | E | 00 | ** BY BHEL RANIPET/EDN | PROFIBUS
112 | 60HFE05CY004 | VT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
113 | 60HFE05CY003 | VT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
114 | 60HFE05CY002 | VT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
115 | 60HFE05CY001 | VT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
116 | 60HFE05CT025 | PT-100 | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
117 | 60HFE05CT026 | PT-100 | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
118 | 60HFE05CT027 | PT-100 | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
849 | 60HNC20CT033 | TT | ID FAN "B" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** | ** | ** | ** | -- | -- | -- | -- | E | 00 | ** BY BHEL RANIPET/EDN | PROFIBUS
851 | 60HNC20CT032 | TT | ID FAN "B" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | D/I,A | ** | ** | ** | ** | -- | -- | -- | -- | E | 00 | ** BY BHEL RANIPET/EDN | PROFIBUS
899 | 60HNC12CQ001 | AT | ID FAN "A" COLD FLUE GAS OUTLET O2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
122 | 60HFE05CT013 | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
123 | 60HFE05CT014 | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
124 | 60HFE05CT015 | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
125 | 60HFE05CT016 | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
126 | 60HFE05CT017 | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
127 | 60HFE05CT018 | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
128 | 60HFE05CT019 | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
129 | 60HFE05CT020 | PT-100 | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
130 | 60HFE05CT021 | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
131 | 60HFE05CT022 | PT-100 | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
132 | 60HFE05CT023 | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
133 | 60HFE05CT024 | PT-100 | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
900 | 60HNC12CQ002 | AT | ID FAN "A" COLD FLUE GAS OUTLET CO2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C |  | -- | % by dry volume | -- | -- | D/I | -- | -- |  | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
907 | 60HNC22CQ001 | AT | ID FAN "B" COLD FLUE GAS OUTLET O2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
908 | 60HNC22CQ002 | AT | ID FAN "B" COLD FLUE GAS OUTLET CO2 | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C |  | -- | % by dry volume | -- | -- | D/I | -- | -- |  | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
917 | 60HNC30CQ007 | AT | FLUE GAS TO STACK O2 | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
996 | 60HAD20CW001 |  | FRONT WALL - LOAD CELL 1 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
997 | 60HAD20CW002 |  | FRONT WALL - LOAD CELL 2 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
998 | 60HAD20CW003 |  | FRONT WALL - LOAD CELL 3 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
999 | 60HAD20CW004 |  | FRONT WALL - LOAD CELL 4 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1000 | 60HAD20CW005 |  | FRONT WALL - LOAD CELL 5 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
143 | 60HFE02CT001 | PT-100 | PA FAN "A" OUTLET AIR TEMP | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
144 | 60HFE06CT001 | PT-100 | PA FAN "B" OUTLET AIR TEMP | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
1001 | 60HAD20CW006 |  | FRONT WALL - LOAD CELL 6 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1002 | 60HAD20CW007 |  | FRONT WALL - LOAD CELL 7 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
147 | 60HFE02CP501 | PI | PA FAN "A" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
148 | 60HFE06CP501 | PI | PA FAN "B" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
149 | 60HFE02CP401 | PP | PA FAN "A" OUTLET AIR PRESS | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
150 | 60HFE06CP401 | PP | PA FAN "B" OUTLET AIR PRESS | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
151 | 60HFE02CT401 | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
152 | 60HFE06CT401 | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
153 | 60HFE02CT402 | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
154 | 60HFE06CT402 | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
155 | 60HFE02CT403 | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
156 | 60HFE06CT403 | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
157 | 60HFE02CT404 | TP | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
158 | 60HFE06CT404 | TP | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
159 | 60HFE02CT405 | TP | APH "A" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
160 | 60HFE02CT406 | TP | APH "A" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
161 | 60HFE02CT407 | TP | APH "A" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
162 | 60HFE02CP402 | PP | APH "A" INLET COLD PA PRESS | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
1003 | 60HAD20CW008 |  | FRONT WALL - LOAD CELL 8 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1004 | 60HAD30CW001 |  | REAR WALL - LOAD CELL 1 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
165 | 60HFE06CT405 | TP | APH "B" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
166 | 60HFE06CT406 | TP | APH "B" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
167 | 60HFE06CT407 | TP | APH "B" INLET COLD PA TEMP | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
168 | 60HFE06CP402 | PP | APH "B" INLET COLD PA PRESS | PA | 1 | -- | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
1005 | 60HAD30CW002 |  | REAR WALL - LOAD CELL 2 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1006 | 60HAD30CW003 |  | REAR WALL - LOAD CELL 3 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
171 | 60HFE03CT401 | TP | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
172 | 60HFE03CT402 | TP | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
173 | 60HFE03CT403 | TP | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
174 | 60HFE03CP401 | PP | APH "A" HOT PA PRESS | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
175 | 60HFE03CT001 | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
176 | 60HFE03CT002 | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
177 | 60HFE03CT003 | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
178 | 60HFE03CT004 | TYPE-K TC | APH "A" HOT PA TEMP | PA | 1 | 3200 x 4300 | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
1007 | 60HAD30CW004 |  | REAR WALL - LOAD CELL 4 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1008 | 60HAD30CW005 |  | REAR WALL - LOAD CELL 5 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1009 | 60HAD30CW006 |  | REAR WALL - LOAD CELL 6 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1010 | 60HAD30CW007 |  | REAR WALL - LOAD CELL 7 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1011 | 60HAD30CW008 |  | REAR WALL - LOAD CELL 8 | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I | -- | -- | 4-20 | mA | -- | -- | -- | -- | T | 00 |  | -
1016 | 60HFE01CG001 | APT | PA FAN - A ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- | -- | 4-20 | mA | 0-100 | % | -- | -- | R | 00 |  | -
185 | 60HFE07CT401 | TP | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
186 | 60HFE07CT402 | TP | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
187 | 60HFE07CT403 | TP | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
188 | 60HFE07CP401 | PP | APH "B" HOT PA PRESS | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
189 | 60HFE07CT001 | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
190 | 60HFE07CT002 | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
191 | 60HFE07CT003 | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
192 | 60HFE07CT004 | TYPE-K TC | APH "B" HOT PA TEMP | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
1017 | 60HFE05CG001 | APT | PA FAN - B ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- | -- | 4-20 | mA | 0-100 | % | -- | -- | R | 00 |  | -
1023 | 60HBK15CG001-009 60HBK25CG001-009 60HBK35CG001-004 60HBK45CG001-004 60HBK10CG001 60HBK30CG001 |  | FURNACE THERMAL EXPANSION MEASUREMENT | DISPLACEMENT | 28 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I |  |  | 4-20 | mA |  |  |  | -- | T | 01
426 | 60HBK10CP002 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  | -- | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
4 | 60HFE01CT031 | TT | PA FAN "A" INLET AIR TEMP | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART
5 | 60HFE01CP002 | PDT | PA FAN "A" DP ACROSS SUCTION & IMPELLER | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
6 | 60HFE01CP003 | PDT | PA FAN "A" STALL DETECTION PROBE | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 | mmWC | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
428 | 60HBK10CP004 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  | -- | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
430 | 60HBK30CP002 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  | -- | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
201 | 60HFE10CP003 | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | F/N,A | ## | mmWC | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 | ## Mill start permissive >635mmWC, <635mmWC mill trip with 5s delay, 508mmWC immediate mill trip | HART
202 | 60HFE10CP004 | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | F/N,A | ## | mmWC | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 | ## Mill start permissive >635mmWC, <635mmWC mill trip with 5s delay, 508mmWC immediate mill trip | HART
203 | 60HFE10CP005 | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | F/N,A | ## | mmWC | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 | ## Mill start permissive >635mmWC, <635mmWC mill trip with 5s delay, 508mmWC immediate mill trip | HART
11 | 60HFE05CT031 | TT | PA FAN "B" INLET AIR TEMP | PA | 1 | -- | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART
205 | 60HLB10CP401 | PP | FD FAN "A" INLET AIR PRESS | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
12 | 60HFE05CP002 | PDT | PA FAN "B" DP ACROSS SUCTION & IMPELLER | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
207 | 60HLB10CT028 | PT-100 | FD FAN "A" INLET AIR TEMP | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
13 | 60HFE05CP003 | PDT | PA FAN "B" STALL DETECTION PROBE | PA | 1 |  | -14 / 1069 | -25 / 1425 | mmWC | 27 / 35 | 50 / 60 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 | mmWC | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
431 | 60HBK30CP003 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  | -- | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
28 | 60HFE01CT001 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
29 | 60HFE01CT002 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
212 | 60HLB20CP401 | PP | FD FAN "B" INLET AIR PRESS | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
30 | 60HFE01CT003 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
214 | 60HLB20CT028 | PT-100 | FD FAN "B" INLET AIR TEMP | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
31 | 60HFE01CT004 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
32 | 60HFE01CT005 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
33 | 60HFE01CT006 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
34 | 60HFE01CT007 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
219 | 60HLB10CY101 | VT | FD FAN "A" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- | -- | -- | -- | -- | -- | -- | -- | E | 00 |  | -
220 | 60HLB10CT001 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
221 | 60HLB10CT002 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
222 | 60HLB10CT003 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
223 | 60HLB10CT004 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
224 | 60HLB10CT005 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
225 | 60HLB10CT006 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
226 | 60HLB10CT007 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
227 | 60HLB10CT008 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
228 | 60HLB10CT009 | PT-100 | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
35 | 60HFE01CT008 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
36 | 60HFE01CT009 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
37 | 60HFE01CT010 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
38 | 60HFE01CT011 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
39 | 60HFE01CT012 | TT | PA FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
45 | 60HFE01CT028 | TT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
46 | 60HFE01CT029 | TT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
47 | 60HFE01CT030 | TT | PA FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
55 | 60HFE01CT025 | TT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
238 | 60HLB10CY005 | VT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
239 | 60HLB10CY006 | VT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
240 | 60HLB10CT010 | PT-100 | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
241 | 60HLB10CT011 | PT-100 | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
242 | 60HLB10CT012 | PT-100 | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
56 | 60HFE01CT026 | TT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
57 | 60HFE01CT027 | TT | PA FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
70 | 60HFE01CT013 | TT | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
246 | 60HLB10CY004 | VT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
247 | 60HLB10CY003 | VT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
248 | 60HLB10CY002 | VT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
249 | 60HLB10CY001 | VT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
250 | 60HLB10CT025 | PT-100 | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
251 | 60HLB10CT026 | PT-100 | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
252 | 60HLB10CT027 | PT-100 | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
71 | 60HFE01CT014 | TT | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
72 | 60HFE01CT019/020 | TT | PA FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
73 | 60HFE01CT015 | TT | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
256 | 60HLB10CT013 | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
257 | 60HLB10CT014 | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
258 | 60HLB10CT015 | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
259 | 60HLB10CT016 | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
260 | 60HLB10CT017 | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
261 | 60HLB10CT018 | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
262 | 60HLB10CT019 | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
263 | 60HLB10CT020 | PT-100 | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
264 | 60HLB10CT021 | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
265 | 60HLB10CT022 | PT-100 | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
266 | 60HLB10CT023 | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
267 | 60HLB10CT024 | PT-100 | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
74 | 60HFE01CT016 | TT | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
75 | 60HFE01CT021/022 | TT | PA FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
76 | 60HFE01CT017 | TT | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
77 | 60HFE01CT018 | TT | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
78 | 60HFE01CT023/024 | TT | PA FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
92 | 60HFE05CT001 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
93 | 60HFE05CT002 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
94 | 60HFE05CT003 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
95 | 60HFE05CT004 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
277 | 60HLB20CY101 | VT | FD FAN "B" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- | -- | -- | -- | -- | -- | -- | -- | E | 00 |  | -
278 | 60HLB20CT001 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
279 | 60HLB20CT002 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
280 | 60HLB20CT003 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
281 | 60HLB20CT004 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
282 | 60HLB20CT005 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
283 | 60HLB20CT006 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
284 | 60HLB20CT007 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
285 | 60HLB20CT008 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
286 | 60HLB20CT009 | PT-100 | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
96 | 60HFE05CT005 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
97 | 60HFE05CT006 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
98 | 60HFE05CT007 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
99 | 60HFE05CT008 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
100 | 60HFE05CT009 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
101 | 60HFE05CT010 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
102 | 60HFE05CT011 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
103 | 60HFE05CT012 | TT | PA FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
109 | 60HFE05CT028 | TT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
296 | 60HLB20CY005 | VT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
297 | 60HLB20CY006 | VT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
298 | 60HLB20CT010 | PT-100 | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
299 | 60HLB20CT011 | PT-100 | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
300 | 60HLB20CT012 | PT-100 | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
110 | 60HFE05CT029 | TT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
111 | 60HFE05CT030 | TT | PA FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
119 | 60HFE05CT025 | TT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
304 | 60HLB20CY004 | VT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
305 | 60HLB20CY003 | VT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
306 | 60HLB20CY002 | VT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
307 | 60HLB20CY001 | VT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
308 | 60HLB20CT025 | PT-100 | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
309 | 60HLB20CT026 | PT-100 | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
310 | 60HLB20CT027 | PT-100 | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
120 | 60HFE05CT026 | TT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
121 | 60HFE05CT027 | TT | PA FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
134 | 60HFE05CT013 | TT | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
314 | 60HLB20CT013 | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
315 | 60HLB20CT014 | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
316 | 60HLB20CT015 | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
317 | 60HLB20CT016 | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
318 | 60HLB20CT017 | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
319 | 60HLB20CT018 | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
320 | 60HLB20CT019 | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
321 | 60HLB20CT020 | PT-100 | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
322 | 60HLB20CT021 | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
323 | 60HLB20CT022 | PT-100 | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
324 | 60HLB20CT023 | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
325 | 60HLB20CT024 | PT-100 | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
135 | 60HFE05CT014 | TT | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
136 | 60HFE05CT019/020 | TT | PA FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
137 | 60HFE05CT015 | TT | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
138 | 60HFE05CT016 | TT | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
139 | 60HFE05CT021/022 | TT | PA FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
140 | 60HFE05CT017 | TT | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
141 | 60HFE05CT018 | TT | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
142 | 60HFE05CT023/024 | TT | PA FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
145 | 60HFE02CT001 | TT | PA FAN "A" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
335 | 60HLA12CT001 | PT-100 | FD FAN "A" OUTLET AIR TEMP | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
146 | 60HFE06CT001 | TT | PA FAN "B" OUTLET AIR TEMP | PA | 1 | -- | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
337 | 60HLA12CT401 | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
338 | 60HLA12CT402 | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
339 | 60HLA12CT403 | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
340 | 60HLA12CT404 | TP | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
341 | 60HLA12CP501 | PI | FD FAN "A" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
342 | 60HLA12CP401 | PP | FD FAN "A" OUTLET AIR PRESS | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
343 | 60HLA22CT001 | PT-100 | FD FAN "B" OUTLET AIR TEMP | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
432 | 60HBK30CP004 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,C,A |  | -- | -1200 to 1200 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | WIDE RANGE PRESSURE TRANSMITTER | PROFIBUS
345 | 60HLA22CT401 | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
346 | 60HLA22CT402 | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
347 | 60HLA22CT403 | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
348 | 60HLA22CT404 | TP | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
349 | 60HLA22CP501 | PI | FD FAN "B" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
350 | 60HLA22CP401 | PP | FD FAN "B" OUTLET AIR PRESS | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
351 | 60HLA13CT401 | TP | APH "A" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
352 | 60HLA13CT402 | TP | APH "A" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
353 | 60HLA13CT403 | TP | APH "A" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
354 | 60HLA13CP401 | PP | APH "A" INLET COLD SA AIR PRESS | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
355 | 60HLA13CT001 | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
356 | 60HLA13CT002 | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
357 | 60HLA13CT003 | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
358 | 60HLA13CT004 | PT-100 | APH "A" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
164 | 60HFE02CP002 | PDT | APH "A" COLD TO HOT PA DIFF. PRESS. | PA | 1 | 3450 x 3450 / 3200 x 4300 | 1048 / 1009 | 1385 / 1330 | mmWC | 35 / 323 | 60 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
453 | 60HBK10CP005 | PT | BEFORE REAR PLATEN SH FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
170 | 60HFE06CP002 | PDT | APH "B" COLD TO HOT PA DIFF. PRESS. | PA | 1 | 3450 x 3450 / 3200 x 4300 | 1048 / 1009 | 1385 / 1330 | mmWC | 35 / 323 | 60 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
179 | 60HFE03CT001 | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
180 | 60HFE03CT002 | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
364 | 60HLA23CT401 | TP | APH "B" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
365 | 60HLA23CT402 | TP | APH "B" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
366 | 60HLA23CT403 | TP | APH "B" INLET COLD SA AIR TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
367 | 60HLA23CP401 | PP | APH "B" INLET COLD SA AIR PRESS | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
368 | 60HLA23CT001 | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
369 | 60HLA23CT002 | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
370 | 60HLA23CT003 | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
371 | 60HLA23CT004 | PT-100 | APH "B" INLET COLD SA TEMP | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | 16 | 200 | -- | -- | -- | 0 to 75 | °C | -- | -- | -- |  | P | 00 |  | -
181 | 60HFE03CT003 | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
182 | 60HFE03CT004 | TT | APH "A" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
454 | 60HBK30CP005 | PT | BEFORE REAR PLATEN SH FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
465 | 60HBK10CP006 | PT | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
193 | 60HFE07CT001 | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
194 | 60HFE07CT002 | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
195 | 60HFE07CT003 | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
196 | 60HFE07CT004 | TT | APH "B" HOT PA TEMP | PA | 1 | -- | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
466 | 60HBK30CP006 | PT | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
381 | 60HLA14CT401 | TP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
382 | 60HLA14CT402 | TP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
383 | 60HLA14CT403 | TP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
384 | 60HLA14CP401 | PP | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
385 | 60HLA14CT001 | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
386 | 60HLA14CT002 | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
387 | 60HLA14CT003 | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
388 | 60HLA14CT004 | TYPE-K TC | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
475 | 60HBK10CP007 | PT | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
199 | 60HFE10CP001 | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | D/I,C | -- | -- | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
200 | 60HFE10CP002 | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | D/I,C | -- | -- | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
204 | 60HFE10CP006 | PDT | FURN TO HOT PA DUCT | FLUE GAS/HOT PY. AIR | 1 |  | -5 / 913 | -17 / 1175 | mmWC | 1153 / 323 | 1164 / 340 | °C | 676-1058 | -- | mmWC | -- | -- | D/I,C | -- | -- | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
476 | 60HBK30CP007 | PT | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
208 | 60HLB10CT028 | TT | FD FAN "A" INLET AIR TEMP | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART
395 | 60HLA24CT401 | TP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
396 | 60HLA24CT402 | TP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
397 | 60HLA24CT403 | TP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
398 | 60HLA24CP401 | PP | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
399 | 60HLA24CT001 | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
400 | 60HLA24CT002 | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
401 | 60HLA24CT003 | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
402 | 60HLA24CT004 | TYPE-K TC | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
209 | 60HLB10CP002 | PDT | FD FAN "A" DP ACROSS SUCTION & IMPELLER | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
210 | 60HLB10CP003 | PDT | FD FAN "A" STALL DETECTION PROBE | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 | mmWC | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
485 | 60HBK10CP008 | PT | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
486 | 60HBK30CP008 | PT | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -100 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
215 | 60HLB20CT028 | TT | FD FAN "B" INLET AIR TEMP | SA | 1 | -- | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART
216 | 60HLB20CP002 | PDT | FD FAN "B" DP ACROSS SUCTION & IMPELLER | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
409 | 60HLA15CF501 | FE | HOT SA "A" AIR | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | DP=99.2 | -- | mmWC | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00 | Refer FE characteristics | -
217 | 60HLB20CP003 | PDT | FD FAN "B" STALL DETECTION PROBE | SA | 1 |  | -13 / 314 | -25 / 460 | mmWC | 27 / 30 | 50 / 55 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 | mmWC | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
495 | 60HBK10CP009 | PT | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
412 | 60HLA25CF501 | FE | HOT SA "B" AIR | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | DP=99.2 | -- | mmWC | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00 | Refer FE characteristics | -
229 | 60HLB10CT001 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
230 | 60HLB10CT002 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
415 | 60HLA15CT001 | TYPE-K TC | HOT SA FROM APH "A" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
416 | 60HLA15CT002 | TYPE-K TC | HOT SA FROM APH "A" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
231 | 60HLB10CT003 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
232 | 60HLB10CT004 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
419 | 60HLA15CP401 | PP | HOT SA FROM APH "A" PRESS | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
420 | 60HLA25CT001 | TYPE-K TC | HOT SA FROM APH "B" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
421 | 60HLA25CT002 | TYPE-K TC | HOT SA FROM APH "B" | SA | 1 |  | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | 16 | 210 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- |  | P | 00 |  | -
233 | 60HLB10CT005 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
234 | 60HLB10CT006 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
424 | 60HLA25CP401 | PP | HOT SA FROM APH 'B" PRESS | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
425 | 60HBK10CP001 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | F/N,A | ## | mmWC | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 | ## High=76.2, Low= -101.6; Very High=152, Very low= -178; Very very low = -228 | HART
235 | 60HLB10CT007 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
427 | 60HBK10CP003 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | F/N,A | ## | mmWC | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 | ## High=76.2, Low= -101.6; Very High=152, Very low= -178; Very very low = -228 | HART
236 | 60HLB10CT008 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
429 | 60HBK30CP001 | PT | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | F/N,A | ## | mmWC | -250 to 250 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 | ## High=76.2, Low= -101.6; Very High=152, Very low= -178; Very very low = -228 | HART
237 | 60HLB10CT009 | TT | FD FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
243 | 60HLB10CT010 | TT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
244 | 60HLB10CT011 | TT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
433 | 60HBK10CP501 | PI | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 | FMG | -
434 | 60HBK30CP501 | PI | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
435 | 60HBK30CP502 | PI | FURNACE PRESS | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 | FMG | -
436 | 60HBK10CT001 | TYPE-K TC | FURNACE TEMP PROBE (LEFT SIDE) | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 1900 | °C | -- | -- | -- | -- | T | 00 |  | -
437 | 60HBK30CT001 | TYPE-K TC | FURNACE TEMP PROBE (RIGHT SIDE) | FLUE GAS | 1 | 21336x19964 | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 1900 | °C | -- | -- | -- | -- | T | 00 |  | -
245 | 60HLB10CT012 | TT | FD FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
253 | 60HLB10CT025 | TT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
440 | 60HBK10CT408 | TP | FURNACE TEMP | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
441 | 60HLA18CP501 | PI | WINDBOX PRESS (LEFT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 | FMG | -
442 | 60HLA28CP501 | PI | WINDBOX PRESS (RIGHT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 | FMG | -
254 | 60HLB10CT026 | TT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
255 | 60HLB10CT027 | TT | FD FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
445 | 60HLA18CP001 | PDT | FURN TO WINDBOX DIFF PRESS (LEFT SIDE) | FLUE GAS / SA | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 102 | -- | mmWC | -- | -- | SA/I,C,N | High alarm=225 | mmWC | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 |  | HART
446 | 60HLA28CP001 | PDT | FURN TO WINDBOX DIFF PRESS (RIGHT SIDE) | FLUE GAS / SA | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 102 | -- | mmWC | -- | -- | SA/I,C,N | High alarm=225 | mmWC | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 |  | HART
447 | 60HHS10CP001 | PDT | SCANNER COOLING AIR / FURN DIFF PRESS | SCA. AIR/FLUE GAS | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 521 | -- | mmWC | -- | -- | F/A,N |  | mmWC | 0 to 800 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 |  | HART
448 | 60HHS10CP002 | PDT | SCANNER COOLING AIR / FURN DIFF PRESS | SCA. AIR/FLUE GAS | 1 |  | -5 / 100 | -17 / 145 | mmWC | 1153 / 331 | 1164 / 340 | °C | 521 | -- | mmWC | -- | -- | F/A,N |  | mmWC | 0 to 800 | mmWC | -- | -- | -- | 1/2" NPT(F) | E | 00 |  | HART
449 | 60HBK10CT401 | TP | BEFORE FRONT PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
450 | 60HBK30CT401 | TP | BEFORE FRONT PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
451 | 60HBK10CT402 | TP | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
452 | 60HBK30CT402 | TP | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
268 | 60HLB10CT013 | TT | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
269 | 60HLB10CT014 | TT | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
455 | 60HBK10CT002 | TYPE-R TC | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1800 | °C | -- | -- | -- |  | P | 00 |  | -
456 | 60HBK30CT002 | TYPE-R TC | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1800 | °C | -- | -- | -- |  | P | 00 |  | -
270 | 60HLB10CT019/020 | TT | FD FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
271 | 60HLB10CT015 | TT | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
272 | 60HLB10CT016 | TT | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
273 | 60HLB10CT021/022 | TT | FD FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
461 | 60HBK10CT403 | TP | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
462 | 60HBK30CT403 | TP | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
463 | 60HBK10CP402 | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
464 | 60HBK30CP402 | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
274 | 60HLB10CT017 | TT | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
275 | 60HLB10CT018 | TT | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
467 | 60HBK10CT003 | TYPE-R TC | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1600 | °C | -- | -- | -- |  | P | 00 |  | -
468 | 60HBK30CT003 | TYPE-R TC | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1600 | °C | -- | -- | -- |  | P | 00 |  | -
276 | 60HLB10CT023/024 | TT | FD FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
287 | 60HLB20CT001 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
471 | 60HBK10CP401 | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
472 | 60HBK30CP401 | PP | FINISH RH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
473 | 60HBK10CT404 | TP | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
474 | 60HBK30CT404 | TP | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
288 | 60HLB20CT002 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
289 | 60HLB20CT003 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
477 | 60HBK10CT004 | TYPE-R TC | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1500 | °C | -- | -- | -- |  | P | 00 |  | -
478 | 60HBK30CT004 | TYPE-R TC | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x19964 | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1500 | °C | -- | -- | -- |  | P | 00 |  | -
290 | 60HLB20CT004 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
291 | 60HLB20CT005 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
481 | 60HBK10CP403 | PP | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
482 | 60HBK30CP403 | PP | FINISH SH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
483 | 60HBK10CT405 | TP | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
484 | 60HBK30CT405 | TP | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
292 | 60HLB20CT006 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
293 | 60HLB20CT007 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
487 | 60HBK10CT005 | TYPE-R TC | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1200 | °C | -- | -- | -- |  | P | 00 |  | -
488 | 60HBK30CT005 | TYPE-R TC | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 1200 | °C | -- | -- | -- |  | P | 00 |  | -
294 | 60HLB20CT008 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
295 | 60HLB20CT009 | TT | FD FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
491 | 60HBK10CP404 | PP | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
492 | 60HBK30CP404 | PP | LTRH INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
493 | 60HBK10CT406 | TP | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
494 | 60HBK30CT406 | TP | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
301 | 60HLB20CT010 | TT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
302 | 60HLB20CT011 | TT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
497 | 60HBK10CT006 | TYPE-K TC | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 700 | °C | -- | -- | -- |  | P | 00 |  | -
498 | 60HBK30CT006 | TYPE-K TC | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 700 | °C | -- | -- | -- |  | P | 00 |  | -
303 | 60HLB20CT012 | TT | FD FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
311 | 60HLB20CT025 | TT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
501 | 60HBK10CP405 | PP | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
502 | 60HBK30CP405 | PP | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
503 | 60HBK10CT407 | TP | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
504 | 60HBK30CT407 | TP | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
312 | 60HLB20CT026 | TT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
313 | 60HLB20CT027 | TT | FD FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
507 | 60HBK10CT007 | TYPE-K TC | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 700 | °C | -- | -- | -- |  | P | 00 |  | -
508 | 60HBK30CT007 | TYPE-K TC | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | 12 | 325 | -- | -- | -- | 0 to 700 | °C | -- | -- | -- |  | P | 00 |  | -
326 | 60HLB20CT013 | TT | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
327 | 60HLB20CT014 | TT | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
511 | 60HBK10CP406 | PP | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
512 | 60HBK30CP406 | PP | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
328 | 60HLB20CT019/020 | TT | FD FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
329 | 60HLB20CT015 | TT | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
515 | 60HNA01CT001 | TYPE-K TC | ECON OUTLET HOPPER-1 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
330 | 60HLB20CT016 | TT | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
331 | 60HLB20CT021/022 | TT | FD FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
332 | 60HLB20CT017 | TT | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
519 | 60HNA01CT002 | TYPE-K TC | ECON OUTLET HOPPER-2 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
333 | 60HLB20CT018 | TT | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
334 | 60HLB20CT023/024 | TT | FD FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
336 | 60HLA12CT001 | TT | FD FAN "A" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
523 | 60HNA02CT001 | TYPE-K TC | ECON OUTLET HOPPER-3 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
344 | 60HLA22CT001 | TT | FD FAN "B" OUTLET AIR TEMP | SA | 1 | -- | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
359 | 60HLA13CT001 | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
360 | 60HLA13CT002 | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
527 | 60HNA02CT002 | TYPE-K TC | ECON OUTLET HOPPER-4 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
361 | 60HLA13CT003 | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
529 | 60HNA10CP401 | PP | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
362 | 60HLA13CT004 | TT | APH "A" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
531 | 60HNA10CT001 | TYPE-K TC | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
496 | 60HBK30CP009 | PT | ECON INLET FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
533 | 60HNA10CT401 | TP | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
372 | 60HLA23CT001 | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
373 | 60HLA23CT002 | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
374 | 60HLA23CT003 | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
537 | 60HNA10CQ401-407 | AP | ECON OUTLET FLUE GAS ANALYSER POCKET | FLUE GAS | 7 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
538 | 60HNA20CP401 | PP | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
375 | 60HLA23CT004 | TT | APH "B" INLET COLD SA TEMP | SA | 1 | -- | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 75 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
540 | 60HNA20CT001 | TYPE-K TC | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
505 | 60HBK10CP010 | PT | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
542 | 60HNA20CT401 | TP | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
377 | 60HLA13CP002 | PDT | APH "A" COLD TO HOT SA DIFF. PRESS. | SA | 1 |  | 279 / 199 | 395 / 295 | mmWC | 30 / 331 | 55 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
378 | 60HLA23CP002 | PDT | APH "B" COLD TO HOT SA DIFF. PRESS. | SA | 1 |  | 279 / 199 | 395 / 295 | mmWC | 30 / 331 | 55 / 340 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 300 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
506 | 60HBK30CP010 | PT | ECON INTERMEDIATE BANK FLUE GAS PRESS | FLUE GAS | 1 | 21336x17678 | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -150 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
546 | 60HNA20CQ401-407 | AP | ECON OUTLET FLUE GAS ANALYSER POCKET | FLUE GAS | 7 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
530 | 60HNA10CP001 | PT | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
389 | 60HLA14CT001 | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
549 | 60HNA10CT002 | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-1 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
390 | 60HLA14CT002 | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
391 | 60HLA14CT003 | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
392 | 60HLA14CT004 | TT | APH "A" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
553 | 60HNA10CT003 | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-2 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
539 | 60HNA20CP001 | PT | ECON OUTLET FLUE GAS PRESS | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
573 | 60HNA31CP001 | PT | AH-A FLUE GAS INLET PRESS | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
403 | 60HLA24CT001 | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
557 | 60HNA10CT004 | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-3 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
404 | 60HLA24CT002 | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
405 | 60HLA24CT003 | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
406 | 60HLA24CT004 | TT | APH "B" OUTLET HOT SA | SA | 1 | -- | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
561 | 60HNA20CT002 | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-4 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
588 | 60HNA41CP001 | PT | AH-B FLUE GAS INLET PRESS | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -200 to 100 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
656 | 60HNA32CP001 | PT | AH-A FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -500 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
410 | 60HLA15CF001 | FT | HOT SA "A" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- | -- | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 00 | Refer FE characteristics | HART
565 | 60HNA20CT003 | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-5 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
411 | 60HLA15CF002 | FT | HOT SA "A" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- | -- | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 00 | Refer FE characteristics | HART
413 | 60HLA25CF001 | FT | HOT SA "B" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- | -- | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 00 | Refer FE characteristics | HART
414 | 60HLA25CF002 | FT | HOT SA "B" AIR | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | F=959.5 | -- | t/h | -- | -- | D/I,C | -- | -- | 0 to 125 | mmWC | 0 to 1100 | t/h | -- | 1/2" NPT(F) | P | 00 | Refer FE characteristics | HART
569 | 60HNA20CT004 | TYPE-K TC | ECO OUTLET DUCT (SCR INLET) HOPPER-6 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00 |  | -
417 | 60HLA15CT001 | TT | HOT SA FROM APH "A" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | HART
418 | 60HLA15CT002 | TT | HOT SA FROM APH "A" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | HART
422 | 60HLA25CT001 | TT | HOT SA FROM APH "B" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | HART
423 | 60HLA25CT002 | TT | HOT SA FROM APH "B" | SA | 1 | -- | 163 | 255 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | HART
574 | 60HNA31CT001 | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
575 | 60HNA31CT002 | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
576 | 60HNA31CT003 | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
577 | 60HNA31CT004 | TYPE-K TC | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
669 | 60HNA42CP001 | PT | AH-B FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -500 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
739 | 60HNC10CP001 | PT | ID FAN "A" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -600 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
744 | 60HNC10CP004 | PT | ID FAN "A" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
749 | 60HNC20CP001 | PT | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -600 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
582 | 60HNA31CP401 | PP | AH-A FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
583 | 60HNA31CT401 | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
584 | 60HNA31CT402 | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
585 | 60HNA31CT403 | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
586 | 60HNA31CT404 | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
587 | 60HNA31CT405 | TP | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
754 | 60HNC20CP004 | PT | ID FAN "B" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
589 | 60HNA41CT001 | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
590 | 60HNA41CT002 | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
591 | 60HNA41CT003 | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
592 | 60HNA41CT004 | TYPE-K TC | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 |  | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | 13 | 230 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- |  | P | 00 |  | -
438 | 60HBK10CT001 | TT | FURNACE TEMP PROBE (LEFT SIDE) | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,N | >593 | °C | 0 to 1900 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | HART
439 | 60HBK30CT001 | TT | FURNACE TEMP PROBE (RIGHT SIDE) | FLUE GAS | 1 | -- | -5 | -17 | mmWC | 1153 | 1164 | °C | -- | -- | -- | -- | -- | D/I,N | >593 | °C | 0 to 1900 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | HART
2 | 60HFE01CP001 | PT | PA FAN "A" INLET AIR PRESS | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
7 | 60HFE01CP004 | PT | PA FAN "A" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
597 | 60HNA41CP401 | PP | AH-B FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
598 | 60HNA41CT401 | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
599 | 60HNA41CT402 | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
600 | 60HNA41CT403 | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
601 | 60HNA41CT404 | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
602 | 60HNA41CT405 | TP | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
9 | 60HFE05CP001 | PT | PA FAN "B" INLET AIR PRESS | PA | 1 |  | -14 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
14 | 60HFE05CP004 | PT | PA FAN "B" OUTLET AIR PRESS | PA | 1 | 3450 x 3450 | 1069 | 1425 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
457 | 60HBK10CT002 | TT | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1800 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
458 | 60HBK30CT002 | TT | BEFORE REAR PLATEN SH FLUE GAS TEMP | FLUE GAS | 1 | -- | -6 | -18 | mmWC | 1045 | 1052 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1800 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
459 | 60HBK10CQ001 | AT | BEFORE REAR PLATEN SH FLUE GAS OXYGEN | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
460 | 60HBK30CQ001 | AT | BEFORE REAR PLATEN SH FLUE GAS OXYGEN | FLUE GAS | 1 | 21336x19964 | -6 | -18 | mmWC | 1045 | 1052 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
163 | 60HFE02CP001 | PT | APH "A" INLET COLD PA PRESS | PA | 1 | 3450 x 3450 | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
169 | 60HFE06CP001 | PT | APH "B" INLET COLD PA PRESS | PA | 1 | 3450 x 3450 | 1048 | 1385 | mmWC | 35 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1800 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
469 | 60HBK10CT003 | TT | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
470 | 60HBK30CT003 | TT | FINISH RH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -7 | -19 | mmWC | 951 | 955 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
183 | 60HFE03CP002 | PT | APH "A" HOT PA PRESS | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
197 | 60HFE07CP002 | PT | APH "B" HOT PA PRESS | PA | 1 |  | 1009 | 1330 | mmWC | 323 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
479 | 60HBK10CT004 | TT | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
480 | 60HBK30CT004 | TT | FINISH SH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -8 | -20 | mmWC | 871 | 874 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
206 | 60HLB10CP001 | PT | FD FAN "A" INLET AIR PRESS | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
211 | 60HLB10CP004 | PT | FD FAN "A" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
489 | 60HBK10CT005 | TT | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
490 | 60HBK30CT005 | TT | LTRH INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -16 | -38 | mmWC | 736 | 736 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 1200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
213 | 60HLB20CP001 | PT | FD FAN "B" INLET AIR PRESS | SA | 1 |  | -13 | -25 | mmWC | 27 | 50 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | -60 to 0 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
218 | 60HLB20CP004 | PT | FD FAN "B" OUTLET AIR PRESS | SA | 1 |  | 314 | 460 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | HART
499 | 60HBK10CT006 | TT | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 700 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
500 | 60HBK30CT006 | TT | ECON INLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 700 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
363 | 60HLA13CP001 | PT | APH "A" INLET COLD SA PRESS | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
376 | 60HLA23CP001 | PT | APH "B" INLET COLD SA PRESS | SA | 1 |  | 279 | 395 | mmWC | 30 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
509 | 60HBK10CT007 | TT | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 700 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
510 | 60HBK30CT007 | TT | ECON INTERMEDIATE BANK FLUE GAS TEMP | FLUE GAS | 1 | -- | -71 | -99 | mmWC | 499 | 502 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 700 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
629 | 60HLD10CT001 | TYPE-K TC | AH-A ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
516 | 60HNA01CT001 | TT | ECON OUTLET HOPPER-1 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
631 | 60HLD10CT002 | TYPE-K TC | AH-A ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
520 | 60HNA01CT002 | TT | ECON OUTLET HOPPER-2 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
633 | 60HLD10CT003 | TYPE-K TC | AH-A ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
524 | 60HNA02CT001 | TT | ECON OUTLET HOPPER-3 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
635 | 60HLD10CT004 | TYPE-K TC | AH-A FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
528 | 60HNA02CT002 | TT | ECON OUTLET HOPPER-4 TEMP | METAL | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
637 | 60HLD10CT005 | TYPE-K TC | AH-A FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
380 | 60HLA14CP002 | PT | APH "A" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
639 | 60HLD10CT006 | TYPE-K TC | AH-A FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
532 | 60HNA10CT001 | TT | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
641 | 60HLD20CT001 | TYPE-K TC | AH-B ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
534 | 60HNA10CQ001 | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
643 | 60HLD20CT002 | TYPE-K TC | AH-B ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
535 | 60HNA10CQ002 | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
645 | 60HLD20CT003 | TYPE-K TC | AH-B ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
536 | 60HNA10CQ003 | AT | ECON OUTLET FLUE GAS CO | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | <100 | -- | ppm | -- | -- | D/I,C | -- | -- | 0 to 500 | ppm | -- | -- | -- | -- | P | 00 |  | -
647 | 60HLD20CT004 | TYPE-K TC | AH-B FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
394 | 60HLA24CP002 | PT | APH "B" OUTLET HOT SA | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
649 | 60HLD20CT005 | TYPE-K TC | AH-B FG O/L DUCT HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
541 | 60HNA20CT001 | TT | ECON OUTLET FLUE GAS TEMP | FLUE GAS | 1 | -- | -107 | -143 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
651 | 60HLD20CT006 | TYPE-K TC | AH-B FG O/L DUCT HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | T | 00 |  | -
543 | 60HNA20CQ001 | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
544 | 60HNA20CQ002 | AT | ECON OUTLET FLUE GAS OXYGEN | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | 3.6 | -- | % by dry volume | -- | -- | D/I,C | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
545 | 60HNA20CQ003 | AT | ECON OUTLET FLUE GAS CO | FLUE GAS | 1 |  | -107 | -143 | mmWC | 355 | 400 | °C | <100 | -- | ppm | -- | -- | D/I,C | -- | -- | 0 to 500 | ppm | -- | -- | -- | -- | P | 00 |  | -
655 | 60HNA32CQ401-407 | AP | AH-A HOT FLUE GAS SAMPLE ANALYSER POCKET | FLUE GAS | 7 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
550 | 60HNA10CT002 | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-1 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
657 | 60HNA32CT401 | TP | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
658 | 60HNA32CT001 | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
659 | 60HNA32CT002 | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
660 | 60HNA32CT003 | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
661 | 60HNA32CT004 | PT-100 | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
554 | 60HNA10CT003 | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-2 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
558 | 60HNA10CT004 | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-3 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
562 | 60HNA20CT002 | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-4 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
566 | 60HNA20CT003 | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-5 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
570 | 60HNA20CT004 | TT | ECO OUTLET DUCT (SCR INLET) HOPPER-6 TEMP | METAL | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
407 | 60HLA20CP001 | PT | HOT SA CROSSOVER DUCT | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
668 | 60HNA42CQ401-407 | AP | AH-B HOT FLUE GAS SAMPLE ANALYSER POCKET | FLUE GAS | 7 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
408 | 60HLA20CP002 | PT | HOT SA CROSSOVER DUCT | SA | 1 |  | 199 | 295 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
670 | 60HNA42CT401 | TP | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
671 | 60HNA42CT001 | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
672 | 60HNA42CT002 | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
673 | 60HNA42CT003 | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
674 | 60HNA42CT004 | PT-100 | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | 13 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
443 | 60HLA18CP002 | PT | WINDBOX PRESS (LEFT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
578 | 60HNA31CT001 | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
579 | 60HNA31CT002 | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
580 | 60HNA31CT003 | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
581 | 60HNA31CT004 | TT | AH-A FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
444 | 60HLA28CP002 | PT | WINDBOX PRESS (RIGHT SIDE) | SA | 1 |  | 100 | 145 | mmWC | 331 | 340 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
681 | 60HNA70CP401 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
682 | 60HNA70CT401 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
683 | 60HNA70CP402 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
684 | 60HNA70CT402 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
685 | 60HNA70CP403 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
686 | 60HNA70CT403 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
687 | 60HNA70CP404 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
688 | 60HNA70CT404 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
689 | 60HNA70CP405 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
690 | 60HNA70CT405 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
691 | 60HNA70CP406 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
692 | 60HNA70CT406 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
693 | 60HNA70CP407 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
694 | 60HNA70CT407 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
695 | 60HNA70CP408 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
696 | 60HNA70CT408 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
697 | 60HNA70CP409 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
698 | 60HNA70CT409 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
699 | 60HNA70CP410 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
700 | 60HNA70CT410 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
701 | 60HNA70CP411 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
702 | 60HNA70CT411 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
703 | 60HNA70CP412 | PP | COLD FLUE GAS TO PRECIP PRESS | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
704 | 60HNA70CT412 | TP | COLD FLUE GAS TO PRECIP TEMP | FLUE GAS | 1 | -- | -306 | -412 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
705 | 60HNC01CT401 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
706 | 60HNC01CP401 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
707 | 60HNC01CT402 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
708 | 60HNC01CP402 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
709 | 60HNC01CT403 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
710 | 60HNC01CP403 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
711 | 60HNC01CT404 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
712 | 60HNC01CP404 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
713 | 60HNC01CT405 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
714 | 60HNC01CP405 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
715 | 60HNC01CT406 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
716 | 60HNC01CP406 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
717 | 60HNC01CT407 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
718 | 60HNC01CP407 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
719 | 60HNC01CT408 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
720 | 60HNC01CP408 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
721 | 60HNC01CT409 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
722 | 60HNC01CP409 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
723 | 60HNC01CT410 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
724 | 60HNC01CP410 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
725 | 60HNC01CT411 | TP | COLD FLUE GAS FROM PRECIP TEMP | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
726 | 60HNC01CP411 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
727 | 60HNC01CT412 | TP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
728 | 60HNC01CP412 | PP | COLD FLUE GAS FROM PRECIP PRESS | FLUE GAS | 1 | -- | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
729 | 60HNC01CQ001 | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- | -- | -- | -- | -- | -- | -- | -- | R | 00 |  | -
730 | 60HNC01CQ002 | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- | -- | -- | -- | -- | -- | -- | -- | R | 00 |  | -
731 | 60HNC01CQ003 | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- | -- | -- | -- | -- | -- | -- | -- | R | 00 |  | -
732 | 60HNC01CQ004 | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- | -- | -- | -- | -- | -- | -- | -- | R | 00 |  | -
733 | 60HNC01CQ005 | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- | -- | -- | -- | -- | -- | -- | -- | R | 00 |  | -
734 | 60HNC01CQ006 | AT | COLD FLUE GAS FROM PRECIP OPACITY | FLUE GAS | 1 | 3000x2450 | -331 | -437 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | E/I | -- | -- | -- | -- | -- | -- | -- | -- | R | 00 |  | -
735 | 60HNC11CP501 | PI | ID FAN "A" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
736 | 60HNC11CT401 | TP | ID FAN "A" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
593 | 60HNA41CT001 | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
738 | 60HNC11CP401 | PP | ID FAN "A" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
594 | 60HNA41CT002 | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
740 | 60HNC10CT031 | PT-100 | ID FAN "A" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
595 | 60HNA41CT003 | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
596 | 60HNA41CT004 | TT | AH-B FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -150 | -202 | mmWC | 355 | 400 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
603 | 60HNA31CP002 | PDT | AH-A FLUE GAS DIFF. PRESS | FLUE GAS | 1 |  | -150 / -251 | -202 / -332 | mmWC | 355 / 131 | 400 / 150 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
604 | 60HNA41CP002 | PDT | AH-B FLUE GAS DIFF. PRESS | FLUE GAS | 1 |  | -150 / -251 | -202 / -332 | mmWC | 355 / 131 | 400 / 150 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 500 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 |  | PROFIBUS
745 | 60HNC21CP501 | PI | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
746 | 60HNC21CT401 | TP | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
630 | 60HLD10CT001 | TT | AH-A ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
748 | 60HNC21CP401 | PP | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
632 | 60HLD10CT002 | TT | AH-A ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
750 | 60HNC20CT031 | PT-100 | ID FAN "B" COLD FLUE GAS INLET PRESS | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
634 | 60HLD10CT003 | TT | AH-A ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
636 | 60HLD10CT004 | TT | AH-A FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
642 | 60HLD20CT001 | TT | AH-B ASH HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
644 | 60HLD20CT002 | TT | AH-B ASH HOPPER-2 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
755 | 60HNC10CY101 | VT | ID FAN "A" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- | -- | -- | -- | -- | -- | -- | -- | E | 00 |  | -
756 | 60HNC10CT001 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
757 | 60HNC10CT002 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
758 | 60HNC10CT003 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
759 | 60HNC10CT004 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
760 | 60HNC10CT005 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
761 | 60HNC10CT006 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
762 | 60HNC10CT007 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
763 | 60HNC10CT008 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
764 | 60HNC10CT009 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
765 | 60HNC10CT010 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
766 | 60HNC10CT011 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
767 | 60HNC10CT012 | PT-100 | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
646 | 60HLD20CT003 | TT | AH-B ASH HOPPER-3 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
648 | 60HLD20CT004 | TT | AH-B FG O/L DUCT HOPPER-1 TEMP | METAL | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 300 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
653 | 60HNA32CQ001 | AT | AH-A FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
654 | 60HNA32CQ002 | AT | AH-A FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
184 | 60HFE03CP001 | PT | SEAL AIR FAN PRESS - APH "A" HOT PA ISOL GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
662 | 60HNA32CT001 | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
663 | 60HNA32CT002 | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
664 | 60HNA32CT003 | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
665 | 60HNA32CT004 | TT | AH-A FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
666 | 60HNA42CQ001 | AT | AH-B FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
667 | 60HNA42CQ002 | AT | AH-B FLUE GAS OUTLET OXYGEN | FLUE GAS | 1 | 5850x8600 | -251 | -332 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
198 | 60HFE07CP001 | PT | SEAL AIR FAN PRESS - APH "B" HOT PA ISOL GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
780 | 60HNC10CT033 | TE | ID FAN "A" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- | -- | ** | ** | -- | -- | -- | -- | R | 00 | ** BY BHEL RANIPET/EDN | -
675 | 60HNA42CT001 | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
782 | 60HNC10CT032 | TE | ID FAN "A" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- | -- | ** | ** | -- | -- | -- | -- | R | 00 | ** BY BHEL RANIPET/EDN | -
676 | 60HNA42CT002 | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
784 | 60HNC10CY005 | VT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
785 | 60HNC10CY006 | VT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
786 | 60HNC10CT028 | PT-100 | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
787 | 60HNC10CT029 | PT-100 | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
788 | 60HNC10CT030 | PT-100 | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
677 | 60HNA42CT003 | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
678 | 60HNA42CT004 | TT | AH-B FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | -251 | -332 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I,C,A | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
737 | 60HNC11CQ001 | AT | ID FAN "A" COLD FLUE GAS INLET O2 | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
792 | 60HNC10CY004 | VT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
793 | 60HNC10CY003 | VT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
794 | 60HNC10CY002 | VT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
795 | 60HNC10CY001 | VT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
796 | 60HNC10CT025 | PT-100 | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
797 | 60HNC10CT026 | PT-100 | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
798 | 60HNC10CT027 | PT-100 | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
379 | 60HLA14CP001 | PT | SEAL AIR FAN PRESS - APH "A" SA O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
741 | 60HNC10CT031 | TT | ID FAN "A" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART
742 | 60HNC10CP002 | PDT | ID FAN "A" DP ACROSS SUCTION & IMPELLER | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
802 | 60HNC10CT013 | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
803 | 60HNC10CT014 | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
804 | 60HNC10CT015 | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
805 | 60HNC10CT016 | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
806 | 60HNC10CT017 | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
807 | 60HNC10CT018 | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
808 | 60HNC10CT019 | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
809 | 60HNC10CT020 | PT-100 | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
810 | 60HNC10CT021 | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
811 | 60HNC10CT022 | PT-100 | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
812 | 60HNC10CT023 | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
813 | 60HNC10CT024 | PT-100 | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
743 | 60HNC10CP003 | PDT | ID FAN "A" STALL DETECTION PROBE | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 | mmWC | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
393 | 60HLA24CP001 | PT | SEAL AIR FAN PRESS - APH "B" SA O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
747 | 60HNC21CQ001 | AT | ID FAN "B" COLD FLUE GAS INLET O2 | FLUE GAS | 1 | 6600x6600 | -386 | -514 | mmWC | 131 | 150 | °C | 5.1 | -- | % by dry volume | -- | -- | D/I | -- | -- | 2 to 10 | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
571 | 60HNA15CP001 | PT | SEAL AIR FAN PRESS AT AH INLET (SCR BYPASS) ISOLATION GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
751 | 60HNC20CT031 | TT | ID FAN "B" COLD FLUE GAS INLET TEMP | FLUE GAS | 1 | -- | -386 | -514 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT DIN RAIL MOUNTED IN JB | HART
752 | 60HNC20CP002 | PDT | ID FAN "B" DP ACROSS SUCTION & IMPELLER | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I | -- | -- | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
753 | 60HNC20CP003 | PDT | ID FAN "B" STALL DETECTION PROBE | FLUE GAS | 1 |  | -386 / 290 | -514 / 396 | mmWC | 131 | 150 | °C |  | -- | mmWC | -- | -- | D/I,A,R | >200 | mmWC | 0 to 1000 | mmWC | -- | -- | -- | 1/2" NPT(F) | P | 00 | # - TP details from Ranipet | HART
572 | 60HNA25CP001 | PT | SEAL AIR FAN PRESS AT AH INLET (SCR BYPASS) ISOLATION GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
768 | 60HNC10CT001 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
823 | 60HNC20CY101 | VT | ID FAN "B" - KEY PHASOR | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | V/I,A,N | -- | -- | -- | -- | -- | -- | -- | -- | E | 00 |  | -
824 | 60HNC20CT001 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
825 | 60HNC20CT002 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
826 | 60HNC20CT003 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
827 | 60HNC20CT004 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
828 | 60HNC20CT005 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
829 | 60HNC20CT006 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
830 | 60HNC20CT007 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
831 | 60HNC20CT008 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
832 | 60HNC20CT009 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
833 | 60HNC20CT010 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
834 | 60HNC20CT011 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
835 | 60HNC20CT012 | PT-100 | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | R | 00 |  | -
769 | 60HNC10CT002 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
770 | 60HNC10CT003 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
771 | 60HNC10CT004 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
772 | 60HNC10CT005 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
773 | 60HNC10CT006 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
774 | 60HNC10CT007 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
775 | 60HNC10CT008 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
776 | 60HNC10CT009 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
777 | 60HNC10CT010 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
778 | 60HNC10CT011 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
779 | 60HNC10CT012 | TT | ID FAN "A" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
789 | 60HNC10CT028 | TT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
848 | 60HNC20CT033 | TE | ID FAN "B" BRG. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- | -- | ** | ** | -- | -- | -- | -- | R | 00 | ** BY BHEL RANIPET/EDN | -
790 | 60HNC10CT029 | TT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
850 | 60HNC20CT032 | TE | ID FAN "B" HYD. ROOM TEMP | METAL | 1 | -- | -- | -- | -- | ** | ** | ** | -- | -- | -- | -- | -- | -- | -- | -- | ** | ** | -- | -- | -- | -- | R | 00 | ** BY BHEL RANIPET/EDN | -
791 | 60HNC10CT030 | TT | ID FAN "A" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
852 | 60HNC20CY005 | VT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
853 | 60HNC20CY006 | VT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | Alarm=4.5, Trip=9 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
854 | 60HNC20CT028 | PT-100 | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
855 | 60HNC20CT029 | PT-100 | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
856 | 60HNC20CT030 | PT-100 | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
799 | 60HNC10CT025 | TT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
800 | 60HNC10CT026 | TT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
801 | 60HNC10CT027 | TT | ID FAN "A" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
860 | 60HNC20CY004 | VT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
861 | 60HNC20CY003 | VT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
862 | 60HNC20CY002 | VT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
863 | 60HNC20CY001 | VT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | -- | -- | -- | <4.5 | -- | mm/s | -- | -- | V/I,A,N | 4.5,7.1 | mm/s |  | mm/s | -- | -- | -- | -- | E | 00 |  | -
864 | 60HNC20CT025 | PT-100 | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
865 | 60HNC20CT026 | PT-100 | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
866 | 60HNC20CT027 | PT-100 | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
814 | 60HNC10CT013 | TT | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
815 | 60HNC10CT014 | TT | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
816 | 60HNC10CT019/020 | TT | ID FAN "A" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
870 | 60HNC20CT013 | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
871 | 60HNC20CT014 | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
872 | 60HNC20CT015 | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
873 | 60HNC20CT016 | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
874 | 60HNC20CT017 | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
875 | 60HNC20CT018 | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
876 | 60HNC20CT019 | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
877 | 60HNC20CT020 | PT-100 | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
878 | 60HNC20CT021 | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
879 | 60HNC20CT022 | PT-100 | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
880 | 60HNC20CT023 | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
881 | 60HNC20CT024 | PT-100 | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | IS | 00 | T = ACTUAL RUNNING TEMP. OBSERVED. | -
817 | 60HNC10CT015 | TT | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
818 | 60HNC10CT016 | TT | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
819 | 60HNC10CT021/022 | TT | ID FAN "A" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
820 | 60HNC10CT017 | TT | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
821 | 60HNC10CT018 | TT | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
822 | 60HNC10CT023/024 | TT | ID FAN "A" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
836 | 60HNC20CT001 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
837 | 60HNC20CT002 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
838 | 60HNC20CT003 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
839 | 60HNC20CT004 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
840 | 60HNC20CT005 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
893 | 60HNC12CP501 | PI | ID FAN "A" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
894 | 60HNC12CP401 | PP | ID FAN "A" COLD FLUE GAS OUTLET PRESS | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
895 | 60HNC12CQ401 | AP | ID FAN "A" COLD FLUE GAS OUTLET ANALYSER POCKET | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
896 | 60HNC12CT401 | TP | ID FAN "A" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
897 | 60HNC12CT001 | PT-100 | ID FAN "A" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
841 | 60HNC20CT006 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
842 | 60HNC20CT007 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
843 | 60HNC20CT008 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
901 | 60HNC22CP501 | PI | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | I | -- | -- |  | mmWC | -- | -- | -- | 1/2" NPT(M) | T | 01 |  | -
902 | 60HNC22CP401 | PP | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
903 | 60HNC22CQ401 | AP | ID FAN "B" COLD FLUE GAS OUTLET ANALYSER POCKET | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
904 | 60HNC22CT401 | TP | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00 |  | -
905 | 60HNC22CT001 | PT-100 | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | 6450x6450 | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | 15 | 50 | -- | -- | -- | 0 to 200 | °C | -- | -- | -- |  | P | 00 |  | -
844 | 60HNC20CT009 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
845 | 60HNC20CT010 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
846 | 60HNC20CT011 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
847 | 60HNC20CT012 | TT | ID FAN "B" BEARING | METAL | 1 | -- | -- | -- | -- | <90 | <110 | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=90, Trip=110 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | PROFIBUS
857 | 60HNC20CT028 | TT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
858 | 60HNC20CT029 | TT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
859 | 60HNC20CT030 | TT | ID FAN "B" MTR DE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
867 | 60HNC20CT025 | TT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
868 | 60HNC20CT026 | TT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
869 | 60HNC20CT027 | TT | ID FAN "B" MTR NDE BEARING | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
882 | 60HNC20CT013 | TT | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
883 | 60HNC20CT014 | TT | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
918 | 60HLA51CF001 | FT | LSOFA CORNER-1 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
919 | 60HLA52CF001 | FT | HSOFA CORNER-4 (FRONT WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
920 | 60HLA61CF001 | FT | LSOFA CORNER-2 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
921 | 60HLA62CF001 | FT | HSOFA CORNER-1 (LEFT WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
922 | 60HLA71CF001 | FT | LSOFA CORNER-3 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
923 | 60HLA72CF001 | FT | HSOFA CORNER-2 (REAR WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
924 | 60HLA81CF001 | FT | LSOFA CORNER-4 FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
925 | 60HLA82CF001 | FT | HSOFA CORNER-3 (RIGHT WALL) FLOW TRANSMITTER | SEC. AIR | 1 | -- |  |  | mmWC |  |  | °C |  | -- | t/h | -- | -- | SA/I,C |  | mmWC | 0-20 | mmWC |  | t/h | -- | -- | E | 00 | Flow element (Multi port Pitot tube) by Trichy | HART
926 | 60HHL95CP106 | PS | HSOFA-C PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
927 | 60HHL95CP105 | PS | HSOFA-B PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
928 | 60HHL95CP104 | PS | HSOFA-A PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
929 | 60HHL95CP103 | PS | LSOFA-C PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
930 | 60HHL95CP102 | PS | LSOFA-B PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
931 | 60HHL95CP101 | PS | LSOFA-A PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
932 | 60HHL91CP104 | PS | EL CCOFA-A SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
933 | 60HHL91CP103 | PS | EL JJ SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
934 | 60HHL91CP102 | PS | EL J SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
935 | 60HHL91CP101 | PS | EL HJJ SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
936 | 60HHL81CP103 | PS | EL HJ SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
937 | 60HHL81CP102 | PS | EL H SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
938 | 60HHL81CP101 | PS | EL GHH SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
939 | 60HHL71CP103 | PS | EL GH SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
940 | 60HHL71CP102 | PS | EL G SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
941 | 60HHL71CP101 | PS | EL FGG SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
942 | 60HHL61CP103 | PS | EL FG SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
943 | 60HHL61CP102 | PS | EL F SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
944 | 60HHL61CP101 | PS | EL EFF SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
945 | 60HHL51CP103 | PS | EL EF SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
946 | 60HHL51CP102 | PS | EL E SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
947 | 60HHL51CP101 | PS | EL DEE SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
948 | 60HHL41CP103 | PS | EL DE SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
949 | 60HHL41CP102 | PS | EL D SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
950 | 60HHL41CP101 | PS | EL CDD SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
951 | 60HHL31CP103 | PS | EL CD SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
952 | 60HHL31CP102 | PS | EL C SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
953 | 60HHL31CP101 | PS | EL BCC SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
954 | 60HHL21CP103 | PS | EL BC SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
955 | 60HHL21CP102 | PS | EL B SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
956 | 60HHL21CP101 | PS | EL ABB SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
957 | 60HHL11CP103 | PS | EL AB SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
958 | 60HHL11CP102 | PS | EL A SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
959 | 60HHL11CP101 | PS | EL AA SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
960 | 60HHL11CP104 | PS | EL AAA SADC PRESS - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | 0.21 | 1.05 | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/N | 0.9 | kg/cm² | -- | -- | -- | -- | -- | -- | E | 00 |  | -
961 | 60HHL95AA106 | I/P | HSOFA-C POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
962 | 60HHL95AA105 | I/P | HSOFA-B POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
963 | 60HHL95AA104 | I/P | HSOFA-A POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
964 | 60HHL95AA103 | I/P | LSOFA-C POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
965 | 60HHL95AA102 | I/P | LSOFA-B POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
966 | 60HHL95AA101 | I/P | LSOFA-A POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
967 | 60HHL91AA104 | I/P | EL CCOFA-A SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
968 | 60HHL91AA103 | I/P | EL JJ SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
969 | 60HHL91AA102 | I/P | EL J SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
970 | 60HHL91AA101 | I/P | EL HJJ SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
971 | 60HHL81AA103 | I/P | EL HJ SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
972 | 60HHL81AA102 | I/P | EL H SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
973 | 60HHL81AA101 | I/P | EL GHH SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
974 | 60HHL71AA103 | I/P | EL GH SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
975 | 60HHL71AA102 | I/P | EL G SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
976 | 60HHL71AA101 | I/P | EL FGG SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
977 | 60HHL61AA103 | I/P | EL FG SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
978 | 60HHL61AA102 | I/P | EL F SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
979 | 60HHL61AA101 | I/P | EL EFF SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
980 | 60HHL51AA103 | I/P | EL EF SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
981 | 60HHL51AA102 | I/P | EL E SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
982 | 60HHL51AA101 | I/P | EL DEE SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
983 | 60HHL41AA103 | I/P | EL DE SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
984 | 60HHL41AA102 | I/P | EL D SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
985 | 60HHL41AA101 | I/P | EL CDD SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
986 | 60HHL31AA103 | I/P | EL CD SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
987 | 60HHL31AA102 | I/P | EL C SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
988 | 60HHL31AA101 | I/P | EL BCC SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
989 | 60HHL21AA103 | I/P | EL BC SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
990 | 60HHL21AA102 | I/P | EL B SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
991 | 60HHL21AA101 | I/P | EL ABB SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
992 | 60HHL11AA103 | I/P | EL AB SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
993 | 60HHL11AA102 | I/P | EL A SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
994 | 60HHL11AA101 | I/P | EL AA SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
995 | 60HHL11AA104 | I/P | EL AAA SADC POSITIONER - COMM FOR ALL CORNERS | SEC. AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | SA/C | -- | -- | 4-20 | mA | 3-15 | psi | -- | -- | E | 00 |  | -
884 | 60HNC20CT019/020 | TT | ID FAN "B" MTR WINDING, B-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
885 | 60HNC20CT015 | TT | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
886 | 60HNC20CT016 | TT | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
887 | 60HNC20CT021/022 | TT | ID FAN "B" MTR WINDING, Y-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
888 | 60HNC20CT017 | TT | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
889 | 60HNC20CT018 | TT | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
890 | 60HNC20CT023/024 | TT | ID FAN "B" MTR WINDING, R-Ph | METAL | 1 | -- | -- | -- | -- | T | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | Alarm=T+5, Trip= T+10 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB, T = ACTUAL RUNNING TEMP. OBSERVED. | PROFIBUS
891 | 60HNC12CP001 | PT | SEAL AIR FAN PRESS - ID FAN-A O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
892 | 60HNC22CP001 | PT | SEAL AIR FAN PRESS - ID FAN -B O/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
898 | 60HNC12CT001 | TT | ID FAN "A" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
906 | 60HNC22CT001 | TT | ID FAN "B" COLD FLUE GAS OUTLET TEMP | FLUE GAS | 1 | -- | 290 | 396 | mmWC | 131 | 150 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
909 | 60HNC31CP001 | PT | SEAL AIR FAN PRESS - METHANOL ISLAND I/L GATE | SEAL AIR | 1 | -- | -- | -- | mmWC | -- | -- | °C | -- | -- | -- | -- | -- | D/N |  |  | -- | -- | -- | -- | -- | -- | R | 00
910 | 60HNC30CF001 | AT | FLUE GAS FLOW METER AT STACK | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | -- | -- | -- | D/I | -- | -- | -- | -- | -- | -- | -- | -- | P | 00 |  | -
911 | 60HNC30CQ001 | AT | FLUE GAS TO STACK CO2 | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | % by dry volume | -- | -- | D/I | -- | -- |  | % by dry volume | -- | -- | -- | -- | P | 00 |  | -
912 | 60HNC30CQ002 | AT | FLUE GAS TO STACK CO | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | <100 | -- | ppm | -- | -- | D/I | -- | -- | 0 to 500 | ppm | -- | -- | -- | -- | P | 00 |  | -
913 | 60HNC30CQ003 | AT | FLUE GAS TO STACK NOX | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | <146 | -- | ppm | -- | -- | D/I | -- | -- | 0 to 1000 | ppm | -- | -- | -- | -- | P | 00 |  | -
914 | 60HNC30CQ004 | AT | FLUE GAS TO STACK SOX | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C | <35 | -- | ppm | -- | -- | D/I | -- | -- | 0 to 1000 | ppm | -- | -- | -- | -- | P | 00 |  | -
915 | 60HNC30CQ005 | AT | FLUE GAS TO STACK OPACITY | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | ppm | -- | -- | D/I | -- | -- |  | ppm | -- | -- | -- | -- | P | 00 |  | -
916 | 60HNC30CQ006 | AT | FLUE GAS TO STACK Hg | FLUE GAS | 1 | -- | 39 | 40 | mmWC | 131 | 150 | °C |  | -- | mg/Nm3 | -- | -- | D/I | -- | -- |  | mg/Nm³ | -- | -- | -- | -- | P | 00 |  | -
1012 | 60HNC10CG001 | APT | ID FAN - A ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- | -- | 4-20 | mA | 0-100 | % | -- | -- | R | 00 |  | -
1013 | 60HNC20CG001 | APT | ID FAN - B ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- | -- | 4-20 | mA | 0-100 | % | -- | -- | R | 00 |  | -
1014 | 60HLB10CG001 | APT | FD FAN - A ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- | -- | 4-20 | mA | 0-100 | % | -- | -- | R | 00 |  | -
1018 | 60HBB01CT001 to 018 | TYPE-K TC | INSIDE PENT HOUSE TEMPERATURE MEASUREMENT | AIR / GAS | 18 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O. (MTM type) | -
1019 | 60HBB10CT001 to 007, 60HBB20CT001 to 006, 60HBB30CT001 to 007, 60HBB40CT001 to 005 | TYPE-K TC | INSULATION SKIN TEMPERATURE MEASUREMENT | INSULATION | 25 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | T | 00 |  | -
1015 | 60HLB20CG001 | APT | FD FAN - B ANGULAR POSITION TRANSMITTER | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | D/I,N | -- | -- | 4-20 | mA | 0-100 | % | -- | -- | R | 00 |  | -
1021 | 60HBB15CT001 to 005, 60HBB25CT001 to 005, 60HBB35CT001 to 005, 60HBB45CT001 to 005 | TYPE-K TC | AMBIENT TEMPERATURE MEASUREMENT | AMBIENT AIR | 20 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | T | 00 |  | -
1020 | 60HBB10CT001 to 007, 60HBB20CT001 to 006, 60HBB30CT001 to 007, 60HBB40CT001 to 005 | TT | INSULATION SKIN TEMPERATURE MEASUREMENT | INSULATION | 25 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | D/I,A |  | °C |  | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
1022 | 60HBB15CT001 to 005, 60HBB25CT001 to 005, 60HBB35CT001 to 005, 60HBB45CT001 to 005 | TT | AMBIENT TEMPERATURE MEASUREMENT | AMBIENT AIR | 20 | -- |  |  | mmWC |  |  | °C | -- | -- | -- | -- | -- | D/I,A |  | °C |  | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT TT MOUNTED IN JB | PROFIBUS
Note on B111: Tag to be confirmed by BAP
Note on B112: Tag to be confirmed by BAP
Note on B120: Tag to be confirmed by BAP
Note on B121: Tag to be confirmed by BAP
Note on N446: 38-102 in CPT1802
Note on N447: 38-102 in CPT1802
Note on B781: Tag to be confirmed by BAP
Note on B783: Tag to be confirmed by BAP
Note on B849: Tag to be confirmed by BAP
Note on B851: Tag to be confirmed by BAP
Note on F1020: =7+6+7+5
Note on F1023: =7+6+7+5