## Sheet1
TAG_NUMBER | TAG_NUMBER | TYPE_OF_INST | DESCRIPTION | MEDIUM | QTY/BOILER | LINE_SIZE | OP_PRESS | MAX_PRESS | UNIT_OF_PRESS | OP_TEMP | MAX_TEMP | UNIT_OF_TEMP | OP_OTHERS | MAX_OTHERS | UNIT_OF_OTHERS | MAX_VELOCITY (m/sec) | INSULATION_THICKNESS (mm) | FUNCTION | SET POINT | UNIT | RANGE_OF_PY_INST | UNIT_OF_PY_INST | RANGE _OF_SEC_INST | UNIT_OF_SEC_INST | CONTACT ACTION | INST_END_CONN | SCOPE | REVISION | REMARKS | TYPE OF PROTOCOL (HART/PROFIBUS)
60HAC10CT001 | 60HAC10CT001 | TYPE-K TC | ECON INLET BOILER FW TEMP | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | 10 | 150 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60LAB91CT001 | 60LAB91CT001 | TT | FEED WATER LINE DRAIN | METAL | 1 | -- |  |  | kg/cm² |  |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- |  | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC10CT002 | 60HAC10CT002 | TYPE-K TC | ECON INLET BOILER FW TEMP | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | 10 | 150 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAG15CT002 | 60HAG15CT002 | TT | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | -- | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC10CT003 | 60HAC10CT003 | TYPE-K TC | ECON DRAIN TEMP | METAL | 1 | 114.3x20 | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAG15CT003 | 60HAG15CT003 | TT | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | -- | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC20CT001 | 60HAC20CT001 | TYPE-K TC | ECON OUTLET LINK | WATER | 1 | 508x70 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 170 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE WITH EXTENSION LENGTH-30 MTS
60HAG15CT004 | 60HAG15CT004 | TT | WARM UP LINE TO BLR RECIRC SYS TEMP | WATER | 1 | -- | 309.7 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG15CP002 | 60HAG15CP002 | PDT | STARTUP SYSTEM MIXING PIECE | WATER | 1 | 508x70 | 313.8 | 353.5 | kg/cm² | 309 | 348 | °C | 0.2 to 0.5 | -- | kg/cm² | -- | -- | D/I | -- | -- | 0 to 5 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAC20CT002 | 60HAC20CT002 | TYPE-K TC | ECON OUTLET LINK | WATER | 1 | 508x70 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 170 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE WITH EXTENSION LENGTH-30 MTS
60HAG15CT005 | 60HAG15CT005 | TT | BWCP SUCTION LINE | WATER | 1 | -- | 315.2 | 353.5 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CP001 | 60HAG25CP001 | PDT | BOILER WATER CIRC PUMP | WATER | 1 | 508x70 / 406.4x55 | 171.42 | 352.7 | kg/cm² | 309 | 357 | °C |  | -- | kg/cm² | -- | -- | D/I,C,N | Min Head =120 | m | 0 to 25 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAG25CP002 | 60HAG25CP002 | PDT | BOILER WATER CIRC PUMP | WATER | 1 | 508x70 / 406.4x55 | 171.42 | 352.7 | kg/cm² | 309 | 357 | °C |  | -- | kg/cm² | -- | -- | D/I,C,N | Min Head =120 | m | 0 to 25 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAG25CP003 | 60HAG25CP003 | PDT | BOILER WATER CIRC PUMP | WATER | 1 | 508x70 / 406.4x55 | 171.42 | 352.7 | kg/cm² | 309 | 357 | °C |  | -- | kg/cm² | -- | -- | D/I,C,N | Min Head =120 | m | 0 to 25 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAG27CP501 | 60HAG27CP501 | PI | BWCP COOLING WTR SUPPLY PRESS | WATER | 1 | 88.9x5.49 | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HAG27CT001 | 60HAG27CT001 | PT-100 | BWCP COOLING WTR SUPPLY TEMP | WATER | 1 | 88.9x5.49 | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | 8 | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 00
60HAG27CT001 | 60HAG27CT001 | TT | BWCP COOLING WTR SUPPLY TEMP | WATER | 1 | -- | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG27CT501 | 60HAG27CT501 | TI | BWCP COOLING WTR SUPPLY TEMP | WATER | 1 | 88.9x5.49 | 6 | 28.2 | kg/cm² | 38 | 60 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60HAG27CT502 | 60HAG27CT502 | TI | BWCP COOLING WTR RETURN TEMP | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60HAG27CT002 | 60HAG27CT002 | PT-100 | BWCP COOLING WTR RETURN TEMP | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | 8 | -- | -- | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 00
60HAG27CT002 | 60HAG27CT002 | TT | BWCP COOLING WTR RETURN TEMP | WATER | 1 | -- | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 150 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG27CF101 | 60HAG27CF101 | FIS | BWCP COOLING WTR RETURN FLOW | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C |  | -- | m³/h | -- | -- | D/I,A,N | Low Alarm= | m³/h | -- | -- | -- | -- | COD | -- | V | 00
60HAG27CT503 | 60HAG27CT503 | TI | BWCP HEAT BARRIER COOLING WTR RETURN TEMP | WATER | 1 | 33.4x3.38 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60HAG27CF102 | 60HAG27CF102 | FIS | BWCP HEAT BARRIER COOLING WTR RETURN FLOW | WATER | 1 | 33.4x3.38 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C |  | -- | m³/h | -- | -- | D/I,A,N | Low Alarm= | m³/h | -- | -- | -- | -- | COD | -- | V | 00
60HAG27CP502 | 60HAG27CP502 | PI | BWCP COOLING WTR RETURN PRESS (COMMON LINE) | WATER | 1 | 88.9x5.49 | 5.5 | 28.2 | kg/cm² | 48 | 60 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HAG25CT001 | 60HAG25CT001 | TYPE-K TC | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 00
60HAG25CT001 | 60HAG25CT001 | TT | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | ** ΔT = 100 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB. ** PUMP CASING / PUMP WATER SUPPLY LINE ΔT | PROFIBUS
60HAG25CT005 | 60HAG25CT005 | TYPE-K TC | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 00
60HAG25CT005 | 60HAG25CT005 | TT | BCP CASING | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | ** ΔT = 100 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB. ** PUMP CASING / PUMP WATER SUPPLY LINE ΔT | PROFIBUS
60HAG25CT002 | 60HAG25CT002 | TYPE-K TC | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 00
60HAG25CT003 | 60HAG25CT003 | TYPE-K TC | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 00
60HAG25CT004 | 60HAG25CT004 | TYPE-K TC | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | V | 00
60HAG25CT002 | 60HAG25CT002 | TT | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | High Alarm= 63 , High Trip= 66 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CT003 | 60HAG25CT003 | TT | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | High Alarm= 63 , High Trip= 66 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CT004 | 60HAG25CT004 | TT | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A,N | High Alarm= 63 , High Trip= 66 | °C | 0 to 150 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG25CT501 | 60HAG25CT501 | TI | BCP MOTOR CAVITY | METAL | 1 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | V | 00
60LCR25CP501 | 60LCR25CP501 | PI | BOILER RECIR PUMP MOTOR LP FILL WTR PRESS | WATER | 1 | 33.4x4.55 | 28.5 | 50 | kg/cm² | 27 | 55 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LCR25CT501 | 60LCR25CT501 | TI | BOILER RECIR PUMP MOTOR LP FILL WTR TEMP | WATER | 1 | 33.4x4.55 | 28.5 | 50 | kg/cm² | 27 | 55 | °C | -- | -- | -- | 8 | -- | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60LCR25CP101 | 60LCR25CP101 | PDIS | BOILER RECIR PUMP MOTOR LP FILL WTR LINE FILTER DIFF PRESS | WATER | 1 | 33.4x4.55 | 28.5 | 50 | kg/cm² | 27 | 55 | °C | -- | -- | -- | -- | -- | D/I | -- | -- |  | kg/cm² | -- | -- | -- | -- | V | 00
60HAC10CP501 | 60HAC10CP501 | PI | ECON INLET BOILER FW PRESS | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HAC10CP401 | 60HAC10CP401 | PP | ECON INLET BOILER FW PRESS | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAC10CF501 | 60HAC10CF501 | FE | ECON INLET BOILER FW FLOW | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60HAC10CF001 | 60HAC10CF001 | FT | ECON INLET BOILER FW FLOW | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | D/I,A,N | Low Alarm=864.35 Low Trip=800.47 | t/hr | Later | mmWC | 0 to 2600 | t/hr | -- | -- | P | 00 |  | HART
60HAC10CF002 | 60HAC10CF002 | FT | ECON INLET BOILER FW FLOW | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | D/I,A,N | Low Alarm=864.35 Low Trip=800.47 | t/hr | Later | mmWC | 0 to 2600 | t/hr | -- | -- | P | 00 |  | HART
60HAC10CF003 | 60HAC10CF003 | FT | ECON INLET BOILER FW FLOW | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | 2452.8 | 2555 | t/hr | -- | -- | D/I,A,N | Low Alarm=864.35 Low Trip=800.47 | t/hr | Later | mmWC | 0 to 2600 | t/hr | -- | -- | P | 00 |  | HART
60HAC10CP001 | 60HAC10CP001 | PT | ECON INLET BOILER FW PRESS | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAC20CT003 | 60HAC20CT003 | TYPE-K TC | ECON MIXING LINE | WATER | 1 | 711x95 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAC10CT001 | 60HAC10CT001 | TT | ECON INLET BOILER FW TEMP | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAC20CT004 | 60HAC20CT004 | TYPE-K TC | ECON MIXING LINE | WATER | 1 | 711x95 | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | 10 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAC10CT002 | 60HAC10CT002 | TT | ECON INLET BOILER FW TEMP | WATER | 1 | -- | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAC10CT401 | 60HAC10CT401 | TW | ECON INLET BOILER FW TEMP | WATER | 1 | 610x82 | 336.6 | 352.7 | kg/cm² | 309 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAD03CT001 | 60HAD03CT001 | TYPE-K TC | FURN LWR FRONT & REAR INLET HDR DRAIN TEMP | METAL | 1 | 114.3x20 | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAC10CT003 | 60HAC10CT003 | TT | ECON DRAIN TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC11CT001 to 006 | 60HAC11CT001 to 006 | TYPE-K TC | ECON INLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | T | 00
60HAC11CT001 to 006 | 60HAC11CT001 to 006 | TT | ECON INLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAC12CT001 to 006 | 60HAC12CT001 to 006 | TYPE-K TC | ECON OUTLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | T | 00
60HAC12CT001 to 006 | 60HAC12CT001 to 006 | TT | ECON OUTLET HEADER TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD10CT132 | 60HAD10CT132 | TYPE-K TC | FURN INTER. LEFT SIDE HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00
60HAC20CT001 | 60HAC20CT001 | TT | ECON OUTLET LINK | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD20CT141 | 60HAD20CT141 | TYPE-K TC | FURN INTER. FRONT HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00
60HAC20CT002 | 60HAC20CT002 | TT | ECON OUTLET LINK | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD30CT141 | 60HAD30CT141 | TYPE-K TC | FURN INTER. REAR HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00
60HAC20CT003 | 60HAC20CT003 | TT | ECON MIXING LINE | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD40CT132 | 60HAD40CT132 | TYPE-K TC | FURN INTER.RIGHT SIDE HDR DRAIN TEMP. | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00
60HAC20CT004 | 60HAC20CT004 | TT | ECON MIXING LINE | WATER | 1 | -- | 327.9 | 344.4 | kg/cm² | 345 | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD81CT009 | 60HAD81CT009 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | WATER | 1 |  | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | 250 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAD03CT001 | 60HAD03CT001 | TT | FURN LWR FRONT & REAR INLET HDR DRAIN TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 357 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD10CT001 to 019 | 60HAD10CT001 to 019 | TYPE-K TC | LEFT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00
60HAD10CT001 to 019 | 60HAD10CT001 to 019 | TT | LEFT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD10CT020 to 131 | 60HAD10CT020 to 131 | TYPE-K TC | LEFT SPIRAL WALL TUBE | METAL | 112 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAD15CT001 to 019 | 60HAD15CT001 to 019 | TYPE-K TC | LEFT VERT WALL OUTLET TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm (HA) = Refer remarks | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O. HA=511°C FOR TUBE 1. HA=524°C FOR TUBES 23, 45, 67. HA=512°C FOR TUBES 89, 111, 133, 155, 177. HA=524°C FOR TUBES 199, 221, 243, 265, 287, 309, 331, 353, 375, 393.
60HAD15CT020 to 393 | 60HAD15CT020 to 393 | TYPE-K TC | LEFT VERT WALL OUTLET TUBE | METAL | 374 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAD82CT009 | 60HAD82CT009 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | WATER | 1 |  | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | 250 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAD10CT132 | 60HAD10CT132 | TT | FURN INTER. LEFT SIDE HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD20CT001 to 020 | 60HAD20CT001 to 020 | TYPE-K TC | FRONT SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00
60HAD20CT001 to 020 | 60HAD20CT001 to 020 | TT | FRONT SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD20CT021 to 140 | 60HAD20CT021 to 140 | TYPE-K TC | FRONT SPIRAL WALL TUBE | METAL | 120 | -- | -- | -- | kg/cm² |  | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAD25CT001 to 020 | 60HAD25CT001 to 020 | TYPE-K TC | FRONT VERT WALL OUTLET TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm= 510 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAD25CT021 to 420 | 60HAD25CT021 to 420 | TYPE-K TC | FRONT VERT WALL OUTLET TUBE | METAL | 400 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAG15CT001 | 60HAG15CT001 | TYPE-K TC | WTR STORAGE TANK DOWNCOMER TEMP | WATER | 1 | 508x70 | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAD20CT141 | 60HAD20CT141 | TT | FURN INTER. FRONT HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD30CT001 to 020 | 60HAD30CT001 to 020 | TYPE-K TC | REAR SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00
60HAD30CT001 to 020 | 60HAD30CT001 to 020 | TT | REAR SPIRAL WALL TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD30CT021 to 140 | 60HAD30CT021 to 140 | TYPE-K TC | REAR SPIRAL WALL TUBE | METAL | 120 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAD35CT001 to 020 | 60HAD35CT001 to 020 | TYPE-K TC | REAR VERT WALL HANGER TUBE | METAL | 20 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm (HA) = Refer remarks | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O. HA=494°C FOR TUBES 1, 23, 45, 89, 111, 155, 177, 221, 243, 287, 309, 353, 375, 419. HA=496°C FOR TUBES 67, 133, 199, 265, 331, 397.
60HAD35CT021 to 420 | 60HAD35CT021 to 420 | TYPE-K TC | REAR VERT WALL HANGER TUBE | METAL | 400 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAG15CT002 | 60HAG15CT002 | TYPE-K TC | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | 508x70 | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAD30CT141 | 60HAD30CT141 | TT | FURN INTER. REAR HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD40CT001 to 019 | 60HAD40CT001 to 019 | TYPE-K TC | RIGHT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00
60HAD40CT001 to 019 | 60HAD40CT001 to 019 | TT | RIGHT SPIRAL WALL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | F/I,A,N | High Alarm= 471, High Trip= 485 | °C | 0 to 800 | °C | -- | -- | -- | -- | E | 00 | DUAL INPUT TT MOUNTED IN JB | HART
60HAD40CT020 to 131 | 60HAD40CT020 to 131 | TYPE-K TC | RIGHT SPIRAL WALL TUBE | METAL | 112 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAD45CT001 to 019 | 60HAD45CT001 to 019 | TYPE-K TC | RIGHT VERT WALL PANEL TUBE | METAL | 19 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm (HA) = Refer remarks | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O. HA=511°C FOR TUBE 393. HA=524°C FOR TUBES 353, 375. HA=512°C FOR TUBES 243, 265, 287, 309, 331. HA=524°C FOR TUBES 1, 23, 45, 67, 89, 111, 133, 155, 177, 199, 221.
60HAD45CT020 to 393 | 60HAD45CT020 to 393 | TYPE-K TC | RIGHT VERT WALL PANEL TUBE | METAL | 374 | -- | -- | -- | kg/cm² | -- | -- | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAG15CT003 | 60HAG15CT003 | TYPE-K TC | WARM UP THRU AUXILIARY WATER RETURN TEMP | WATER | 1 | 508x70 | 311.2 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAD40CT132 | 60HAD40CT132 | TT | FURN INTER.RIGHT SIDE HDR DRAIN TEMP. | METAL | 1 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH01CP001 | 60HAH01CP001 | PT | WATER SEPARATOR "A" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAG15CT004 | 60HAG15CT004 | TYPE-K TC | WARM UP LINE TO BLR RECIRC SYS TEMP | WATER | 1 | 508x70 | 309.7 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | 5 | 180 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAH01CT001 | 60HAH01CT001 | TT | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH01CT401 | 60HAH01CT401 | TW | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH01CP002 | 60HAH01CP002 | PT | WATER SEPARATOR "A" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAG15CT005 | 60HAG15CT005 | TYPE-K TC | BWCP SUCTION LINE | WATER | 1 | 508x70 | 315.2 | 353.5 | kg/cm² | 309 | 348 | °C | -- | -- | -- | 5 | 150 | -- | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00
60HAH01CT002 | 60HAH01CT002 | TT | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH01CT402 | 60HAH01CT402 | TW | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH01CT001 | 60HAH01CT001 | TYPE-K TC | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH01CT003 | 60HAH01CT003 | TT | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH01CT002 | 60HAH01CT002 | TYPE-K TC | WATER SEPARATOR "A" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH01CT004 | 60HAH01CT004 | TT | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH02CP001 | 60HAH02CP001 | PT | WATER SEPARATOR "B" OUTLET PRESS | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAH01CT003 | 60HAH01CT003 | TYPE-K TC | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAH02CT001 | 60HAH02CT001 | TT | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | -- | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH02CT401 | 60HAH02CT401 | TW | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH02CP002 | 60HAH02CP002 | PT | WATER SEPARATOR "B" OUTLET PRESS | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 500 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAH01CT004 | 60HAH01CT004 | TYPE-K TC | WATER SEPARATOR "A" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAH02CT002 | 60HAH02CT002 | TT | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | -- | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH02CT402 | 60HAH02CT402 | TW | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH02CT001 | 60HAH02CT001 | TYPE-K TC | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | 30 | 240 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH02CT003 | 60HAH02CT003 | TT | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH02CT002 | 60HAH02CT002 | TYPE-K TC | WATER SEPARATOR "B" OUTLET TEMP | STEAM | 1 | 273x50 | 305 | 330 | kg/cm² | 433 | 479 | °C | -- | -- | -- | 30 | --- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH02CT004 | 60HAH02CT004 | TT | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH03CP001 | 60HAH03CP001 | PT | WATER SEPARATOR "C" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAH02CT003 | 60HAH02CT003 | TYPE-K TC | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAH03CT001 | 60HAH03CT001 | TT | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH03CT401 | 60HAH03CT401 | TW | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH03CP002 | 60HAH03CP002 | PT | WATER SEPARATOR "C" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAH02CT004 | 60HAH02CT004 | TYPE-K TC | WATER SEPARATOR "B" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAH03CT002 | 60HAH03CT002 | TT | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH03CT402 | 60HAH03CT402 | TW | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH03CT001 | 60HAH03CT001 | TYPE-K TC | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH03CT003 | 60HAH03CT003 | TT | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH03CT002 | 60HAH03CT002 | TYPE-K TC | WATER SEPARATOR "C" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH03CT004 | 60HAH03CT004 | TT | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH04CP001 | 60HAH04CP001 | PT | WATER SEPARATOR "D" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAH03CT003 | 60HAH03CT003 | TYPE-K TC | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAH04CT001 | 60HAH04CT001 | TT | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH04CT401 | 60HAH04CT401 | TW | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH04CP002 | 60HAH04CP002 | PT | WATER SEPARATOR "D" OUTLET PRESS | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAH03CT004 | 60HAH03CT004 | TYPE-K TC | WATER SEPARATOR "C" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAH04CT002 | 60HAH04CT002 | TT | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | -- | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C,N,A | High Alarm=480 | °C | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH04CT402 | 60HAH04CT402 | TW | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH04CT001 | 60HAH04CT001 | TYPE-K TC | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH04CT003 | 60HAH04CT003 | TT | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH04CT002 | 60HAH04CT002 | TYPE-K TC | WATER SEPARATOR "D" OUTLET TEMP | STEAM | 1 | 273x50 | 307.3 | 322.9 | kg/cm² | 439 | 475 | °C | -- | -- | -- | 30 | 210 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH04CT004 | 60HAH04CT004 | TT | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAD71CT001 | 60HAD71CT001 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT002 | 60HAD71CT002 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT003 | 60HAD71CT003 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT004 | 60HAD71CT004 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT005 | 60HAD71CT005 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT006 | 60HAD71CT006 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT007 | 60HAD71CT007 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT008 | 60HAD71CT008 | TYPE-K TC | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD71CT001 | 60HAD71CT001 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT002 | 60HAD71CT002 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT003 | 60HAD71CT003 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT004 | 60HAD71CT004 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT005 | 60HAD71CT005 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT006 | 60HAD71CT006 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT007 | 60HAD71CT007 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD71CT008 | 60HAD71CT008 | TT | WATER SEPARATOR "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT001 | 60HAD72CT001 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT002 | 60HAD72CT002 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT003 | 60HAD72CT003 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT004 | 60HAD72CT004 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT005 | 60HAD72CT005 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT006 | 60HAD72CT006 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT007 | 60HAD72CT007 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT008 | 60HAD72CT008 | TYPE-K TC | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD72CT001 | 60HAD72CT001 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT002 | 60HAD72CT002 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT003 | 60HAD72CT003 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT004 | 60HAD72CT004 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT005 | 60HAD72CT005 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT006 | 60HAD72CT006 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT007 | 60HAD72CT007 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD72CT008 | 60HAD72CT008 | TT | WATER SEPARATOR "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT001 | 60HAD73CT001 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT002 | 60HAD73CT002 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT003 | 60HAD73CT003 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT004 | 60HAD73CT004 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT005 | 60HAD73CT005 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT006 | 60HAD73CT006 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT007 | 60HAD73CT007 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT008 | 60HAD73CT008 | TYPE-K TC | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD73CT001 | 60HAD73CT001 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT002 | 60HAD73CT002 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT003 | 60HAD73CT003 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT004 | 60HAD73CT004 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT005 | 60HAD73CT005 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT006 | 60HAD73CT006 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT007 | 60HAD73CT007 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD73CT008 | 60HAD73CT008 | TT | WATER SEPARATOR "C" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT001 | 60HAD74CT001 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT002 | 60HAD74CT002 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT003 | 60HAD74CT003 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT004 | 60HAD74CT004 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT005 | 60HAD74CT005 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT006 | 60HAD74CT006 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT007 | 60HAD74CT007 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT008 | 60HAD74CT008 | TYPE-K TC | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD74CT001 | 60HAD74CT001 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT002 | 60HAD74CT002 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT003 | 60HAD74CT003 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT004 | 60HAD74CT004 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT005 | 60HAD74CT005 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT006 | 60HAD74CT006 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT007 | 60HAD74CT007 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD74CT008 | 60HAD74CT008 | TT | WATER SEPARATOR "D" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CL001 | 60HAD81CL001 | LT | SEPARATOR STRG TANK "A" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 00 |  | HART
60HAD81CL002 | 60HAD81CL002 | LT | SEPARATOR STRG TANK "A" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 00 |  | HART
60HAD81CL003 | 60HAD81CL003 | LT | SEPARATOR STRG TANK "A" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 00 |  | HART
60HAD81CP001 | 60HAD81CP001 | PT | SEPARATOR STRG TANK "A" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAD81CP002 | 60HAD81CP002 | PT | SEPARATOR STRG TANK "A" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAD81CT001 | 60HAD81CT001 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD81CT002 | 60HAD81CT002 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD81CT003 | 60HAD81CT003 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD81CT004 | 60HAD81CT004 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD81CT005 | 60HAD81CT005 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD81CT006 | 60HAD81CT006 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD81CT007 | 60HAD81CT007 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD81CT008 | 60HAD81CT008 | TYPE-K TC | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAH04CT003 | 60HAH04CT003 | TYPE-K TC | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAD81CT001 | 60HAD81CT001 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT002 | 60HAD81CT002 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT003 | 60HAD81CT003 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT004 | 60HAD81CT004 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT005 | 60HAD81CT005 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT006 | 60HAD81CT006 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT007 | 60HAD81CT007 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT008 | 60HAD81CT008 | TT | SEPARATOR STRG TANK "A" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD81CT009 | 60HAD81CT009 | TT | SEPARATOR STRG TANK "A" TEMP | WATER | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CL001 | 60HAD82CL001 | LT | SEPARATOR STRG TANK "B" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 00 |  | HART
60HAD82CL002 | 60HAD82CL002 | LT | SEPARATOR STRG TANK "B" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 00 |  | HART
60HAD82CL003 | 60HAD82CL003 | LT | SEPARATOR STRG TANK "B" LEVEL | WATER | 1 | 33.40x9.09 | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | 8.33 | -- | m | -- | -- | D/I,C,N | High Alarm= 14.67 High Trip= 15.67 | m | 0 to 16.67 | m | -- | -- | -- | -- | P | 00 |  | HART
60HAD82CP001 | 60HAD82CP001 | PT | SEPARATOR STRG TANK "B" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAD82CP002 | 60HAD82CP002 | PT | SEPARATOR STRG TANK "B" PRESS | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | HART
60HAD82CT001 | 60HAD82CT001 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD82CT002 | 60HAD82CT002 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD82CT003 | 60HAD82CT003 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD82CT004 | 60HAD82CT004 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD82CT005 | 60HAD82CT005 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD82CT006 | 60HAD82CT006 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD82CT007 | 60HAD82CT007 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAD82CT008 | 60HAD82CT008 | TYPE-K TC | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | T | 00
60HAH04CT004 | 60HAH04CT004 | TYPE-K TC | WATER SEPARATOR "D" OUTLET VENT TEMP | METAL | 1 | 219.1 X 10.31 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAD82CT001 | 60HAD82CT001 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT002 | 60HAD82CT002 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT003 | 60HAD82CT003 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT004 | 60HAD82CT004 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT005 | 60HAD82CT005 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT006 | 60HAD82CT006 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT007 | 60HAD82CT007 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT008 | 60HAD82CT008 | TT | SEPARATOR STRG TANK "B" TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAD82CT009 | 60HAD82CT009 | TT | SEPARATOR STRG TANK "B" TEMP | WATER | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAG11CL001 | 60HAG11CL001 | LT | SEPARATOR STRG TANK "A" DNCOMER LEVEL | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | DP=0.24 | -- | kg/cm² | -- | -- | D/I,C | High Alarm= 0.42 Low Alarm= 0.04 Control=$ | kg/cm² | 0 to 0.8 | kg/cm² | -- | -- | -- | -- | P | 00 | $ - Control set point is middle of F-49 Downcomer | HART
60HAG12CL001 | 60HAG12CL001 | LT | SEPARATOR STRG TANK "B" DNCOMER LEVEL | WATER | 1 | -- | 309.7 | 325.3 | kg/cm² | 439 | 475 | °C | DP=0.24 | -- | kg/cm² | -- | -- | D/I,C | High Alarm= 0.42 Low Alarm= 0.04 Control=$ | kg/cm² | 0 to 0.8 | kg/cm² | -- | -- | -- | -- | P | 00 | $ - Control set point is middle of F-49 Downcomer | HART
60HAH05CT001 | 60HAH05CT001 | TYPE-K TC | SH FURN ROOF INLET HDR DRAIN TEMP | METAL | 1 | 73x14.02 | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAG15CT001 | 60HAG15CT001 | TT | WTR STORAGE TANK DOWNCOMER TEMP | WATER | 1 | -- | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAG15CT401 | 60HAG15CT401 | TW | WTR STORAGE TANK DOWNCOMER TEMP | WATER | 1 | 508x70 | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAG15CP001 | 60HAG15CP001 | PT | WTR STORAGE TANK DOWNCOMER PRESS | WATER | 1 | 508x70 | 309.5 | 326 | kg/cm² | 345 | 374 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH14CT001 | 60HAH14CT001 | TYPE-K TC | BP LOWER FRONT HDR DRAIN TEMP | METAL | 1 | 88.9x20 | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH05CT001 | 60HAH05CT001 | TT | SH FURN ROOF INLET HDR DRAIN TEMP | METAL | 1 | -- | -- | -- | kg/cm² | -- | 475 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH14CT002 | 60HAH14CT002 | TYPE-K TC | BP LOWER REAR HDR DRAIN TEMP | METAL | 1 | 88.9x20 | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00
60HAH14CT001 | 60HAH14CT001 | TT | BP LOWER FRONT HDR DRAIN TEMP | METAL | 1 |  | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH26CT001 | 60HAH26CT001 | TYPE-K TC | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | 457.2x75 | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- |  | 100 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH14CT002 | 60HAH14CT002 | TT | BP LOWER REAR HDR DRAIN TEMP | METAL | 1 |  | -- | -- | kg/cm² | -- | 514 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH26CT002 | 60HAH26CT002 | TYPE-K TC | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | 457.2x75 | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- |  | 100 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH26CT001 | 60HAH26CT001 | TT | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | -- | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH71CT001 | 60HAH71CT001 | TYPE-K TC | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH26CT002 | 60HAH26CT002 | TT | LINK TO SH FRONT PLATEN INLET HEADER TEMP | STEAM | 1 | -- | 301.2 | 319.8 | kg/cm² | 451 | 490 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAH33CT001 to 006 | 60HAH33CT001 to 006 | TYPE-K TC | SH FRONT PLATEN INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH34CT001 to 085 | 60HAH34CT001 to 085 | TYPE-K TC | SH PLATEN FRONT S-27 TUBE TEMP | METAL | 85 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=578 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH34CT086 to 101 | 60HAH34CT086 to 101 | TYPE-K TC | SH PLATEN FRONT TUBE INSIDE GAS PATH TEMP | METAL | 16 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH35CT001 to 012 | 60HAH35CT001 to 012 | TYPE-K TC | SH FONT PLATEN OUTLET HEADER METAL TEMP | METAL | 12 | -- | -- | -- | kg/cm² | -- | <578 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60LAE70CP501 | 60LAE70CP501 | PI | SH / DSH STAGE-I SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 335.25 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE70CP401 | 60LAE70CP401 | PP | SH / DSH STAGE-I SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 335.25 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60LAE70CT501 | 60LAE70CT501 | TI | SH / DSH STAGE-I SPRAY WATER TEMP | WATER | 1 | 163.3x26 | 335.25 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 15 | 100 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60LAE71CP501 | 60LAE71CP501 | PI | SH / DSH STAGE-I "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE71CP001 | 60LAE71CP001 | PT | SH / DSH STAGE-I "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH71CT002 | 60HAH71CT002 | TYPE-K TC | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LAE71CT001 | 60LAE71CT001 | TT | SH / DSH STAGE-I "A" SPRAY WATER TEMP | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE71CF501 | 60LAE71CF501 | FE | SH / DSH STAGE-I "A" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60LAE71CF001 | 60LAE71CF001 | FT | SH / DSH STAGE-I "A" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE71CF002 | 60LAE71CF002 | FT | SH / DSH STAGE-I "A" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE72CP501 | 60LAE72CP501 | PI | SH / DSH STAGE-I "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE72CP001 | 60LAE72CP001 | PT | SH / DSH STAGE-I "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH71CT003 | 60HAH71CT003 | TYPE-K TC | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LAE72CT001 | 60LAE72CT001 | TT | SH / DSH STAGE-I "B" SPRAY WATER TEMP | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE72CF501 | 60LAE72CF501 | FE | SH / DSH STAGE-I "B" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60LAE72CF001 | 60LAE72CF001 | FT | SH / DSH STAGE-I "B" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE72CF002 | 60LAE72CF002 | FT | SH / DSH STAGE-I "B" SPRAY WATER FLOW | WATER | 1 | -- | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | 22 | 66 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60HAH71CT004 | 60HAH71CT004 | TYPE-K TC | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH71CT001 | 60HAH71CT001 | TT | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH71CT005 | 60HAH71CT005 | TYPE-K TC | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH71CT002 | 60HAH71CT002 | TT | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH71CT401 | 60HAH71CT401 | TW | SH / DSH STAGE-I "A" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH72CT001 | 60HAH72CT001 | TYPE-K TC | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH72CT001 | 60HAH72CT001 | TT | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT002 | 60HAH72CT002 | TYPE-K TC | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH72CT002 | 60HAH72CT002 | TT | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | -- | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT401 | 60HAH72CT401 | TW | SH / DSH STAGE-I "B" INLET TEMP | STEAM | 1 | 558.8x80 | 293.9 | 308.7 | kg/cm² | 516 | 541 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH71CP001 | 60HAH71CP001 | PT | SH / DSH STAGE-I "A" OUTLET PRESS | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH71CT402 | 60HAH71CT402 | TW | SH / DSH STAGE-I "A" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH72CT003 | 60HAH72CT003 | TYPE-K TC | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH71CT003 | 60HAH71CT003 | TT | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT004 | 60HAH72CT004 | TYPE-K TC | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH71CT004 | 60HAH71CT004 | TT | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CT005 | 60HAH72CT005 | TYPE-K TC | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH71CT005 | 60HAH71CT005 | TT | SH / DSH STAGE-I"A" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH72CP001 | 60HAH72CP001 | PT | SH / DSH STAGE-I "B" OUTLET PRESS | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH72CT402 | 60HAH72CT402 | TW | SH / DSH STAGE-I "B" OUTLET TEMP | STEAM | 1 | 558.8x75 | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH91CT001 | 60HAH91CT001 | TYPE-K TC | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH72CT003 | 60HAH72CT003 | TT | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH91CT002 | 60HAH91CT002 | TYPE-K TC | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH72CT004 | 60HAH72CT004 | TT | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH91CT003 | 60HAH91CT003 | TYPE-K TC | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH72CT005 | 60HAH72CT005 | TT | SH / DSH STAGE-I"B" OUTLET TEMP | STEAM | 1 | -- | 292.6 | 308.7 | kg/cm² | 507 | 531 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH37CT001 to 006 | 60HAH37CT001 to 006 | TYPE-K TC | SH REAR PLATEN INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH36CT001 to 085 | 60HAH36CT001 to 085 | TYPE-K TC | SH PLATEN REAR S-33 TUBE TEMP | METAL | 85 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=626 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH36CT086 to 101 | 60HAH36CT086 to 101 | TYPE-K TC | SH REAR PLATEN TUBE INSIDE GAS PASS TEMP | METAL | 16 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH38CT001 to 012 | 60HAH38CT001 to 012 | TYPE-K TC | SH REAR PLATEN OUTLET HEADER METAL TEMP | METAL | 12 | -- | -- | -- | kg/cm² | -- | <626 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60LAE90CP501 | 60LAE90CP501 | PI | SH / DSH STAGE-II SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 334.9 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE90CP401 | 60LAE90CP401 | PP | SH / DSH STAGE-II SPRAY WATER PRESS | WATER | 1 | 168.3x26 | 334.9 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60LAE90CT501 | 60LAE90CT501 | TI | SH / DSH STAGE-II SPRAY WATER TEMP | WATER | 1 | 168.3x26 | 334.9 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 15 | 100 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60LAE91CP501 | 60LAE91CP501 | PI | SH / DSH STAGE-II "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE91CP001 | 60LAE91CP001 | PT | SH / DSH STAGE-II "A" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH91CT004 | 60HAH91CT004 | TYPE-K TC | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LAE91CT001 | 60LAE91CT001 | TT | SH / DSH STAGE-II "A" SPRAY WATER TEMP | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE91CF501 | 60LAE91CF501 | FE | SH / DSH STAGE-II "A" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60LAE91CF001 | 60LAE91CF001 | FT | SH / DSH STAGE-II "A" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE91CF002 | 60LAE91CF002 | FT | SH / DSH STAGE-II "A" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE92CP501 | 60LAE92CP501 | PI | SH / DSH STAGE-II "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE92CP001 | 60LAE92CP001 | PT | SH / DSH STAGE-II "B" SPRAY WATER PRESS | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH91CT005 | 60HAH91CT005 | TYPE-K TC | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LAE92CT001 | 60LAE92CT001 | TT | SH / DSH STAGE-II "B" SPRAY WATER TEMP | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE92CF501 | 60LAE92CF501 | FE | SH / DSH STAGE-II "B" SPRAY WATER FLOW | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60LAE92CF001 | 60LAE92CF001 | FT | SH / DSH STAGE-II "B" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE92CF002 | 60LAE92CF002 | FT | SH / DSH STAGE-II "B" SPRAY WATER FLOW | WATER | 1 | -- | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | 29.1 | 87.3 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60HAH92CT001 | 60HAH92CT001 | TYPE-K TC | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH91CT001 | 60HAH91CT001 | TT | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CT002 | 60HAH92CT002 | TYPE-K TC | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | 35 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH91CT002 | 60HAH91CT002 | TT | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH91CT401 | 60HAH91CT401 | TW | SH / DSH STAGE-II "A" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH92CT003 | 60HAH92CT003 | TYPE-K TC | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH92CT001 | 60HAH92CT001 | TT | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CT004 | 60HAH92CT004 | TYPE-K TC | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH92CT002 | 60HAH92CT002 | TT | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | -- | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CT401 | 60HAH92CT401 | TW | SH / DSH STAGE-II "B" INLET TEMP | STEAM | 1 | 558.8x85 | 284.7 | 299.0 | kg/cm² | 558 | 584 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH91CP001 | 60HAH91CP001 | PT | SH / DSH STAGE-II"A" OUTLET PRESS | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH91CT402 | 60HAH91CT402 | TW | SH / DSH STAGE-II "A" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAH92CT005 | 60HAH92CT005 | TYPE-K TC | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | 30 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH91CT003 | 60HAH91CT003 | TT | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT001 | 60HAJ21CT001 | TYPE-K TC | RH / DSH "A" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH91CT004 | 60HAH91CT004 | TT | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT002 | 60HAJ21CT002 | TYPE-K TC | RH / DSH "A" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH91CT005 | 60HAH91CT005 | TT | SH / DSH STAGE-II"A" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH92CP001 | 60HAH92CP001 | PT | SH / DSH STAGE-II"B" OUTLET PRESS | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 400 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60HAH92CT402 | 60HAH92CT402 | TW | SH / DSH STAGE-II "B" OUTLET TEMP | STEAM | 1 | 558.8x80 | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAJ21CT003 | 60HAJ21CT003 | TYPE-K TC | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH92CT003 | 60HAH92CT003 | TT | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT004 | 60HAJ21CT004 | TYPE-K TC | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH92CT004 | 60HAH92CT004 | TT | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT005 | 60HAJ21CT005 | TYPE-K TC | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60HAH92CT005 | 60HAH92CT005 | TT | SH / DSH STAGE-II"B" OUTLET TEMP | STEAM | 1 | -- | 283.2 | 299.0 | kg/cm² | 545 | 564 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAH39CT001 to 006 | 60HAH39CT001 to 006 | TYPE-K TC | SH FINISH INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH40CT001 to 104 | 60HAH40CT001 to 104 | TYPE-K TC | SH FINISH INLET TUBE OUTSIDE FLUE GAS PATH METAL TEMP | METAL | 104 | -- | -- | -- | kg/cm² | -- | 564 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH41CT001 to 134 | 60HAH41CT001 to 134 | TYPE-K TC | SH FINISH OUTLET TUBE OUTSIDE FLUE GAS PATH METAL TEMP | METAL | 134 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=644 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH41CT135 to 152 | 60HAH41CT135 to 152 | TYPE-K TC | SH FINISH OUTLET TUBE INSIDE FLUE GAS PATH METAL TEMP | METAL | 18 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH42CT001 to 009 | 60HAH42CT001 to 009 | TYPE-K TC | SH FINISH OUTLET HEADER-1 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH42CT010 to 015 | 60HAH42CT010 to 015 | TYPE-K TC | SH FINISH OUTLET HEADER-1 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-1 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAH42CT016 to 024 | 60HAH42CT016 to 024 | TYPE-K TC | SH FINISH OUTLET HEADER-2 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH42CT025 to 030 | 60HAH42CT025 to 030 | TYPE-K TC | SH FINISH OUTLET HEADER-2 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-2 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAH42CT031 to 039 | 60HAH42CT031 to 039 | TYPE-K TC | SH FINISH OUTLET HEADER-3 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH42CT040 to 045 | 60HAH42CT040 to 045 | TYPE-K TC | SH FINISH OUTLET HEADER-3 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-3 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAH42CT046 to 054 | 60HAH42CT046 to 054 | TYPE-K TC | SH FINISH OUTLET HEADER-4 METAL TEMP (BOSMON) | METAL | 9 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAH42CT055 to 060 | 60HAH42CT055 to 060 | TYPE-K TC | SH FINISH OUTLET HEADER-4 METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
-- | -- | TYPE-K TC | SH FINISH OUTLET HEADER-4 METAL TEMP (LOOSE SUPPLY) | METAL | 15 | -- | -- | -- | kg/cm² | -- | <644 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | SUPPLIED AS LOOSE ITEM. NOT TO BE ERECTED.
60HAJ22CT001 | 60HAJ22CT001 | TYPE-K TC | RH / DSH "B" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LBA11CT001 | 60LBA11CT001 | TT | SH FINISH OUTLET VENT-1 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ22CT002 | 60HAJ22CT002 | TYPE-K TC | RH / DSH "B" INLET | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LBA11CT002 | 60LBA11CT002 | TT | SH FINISH OUTLET VENT-2 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ22CT003 | 60HAJ22CT003 | TYPE-K TC | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LBA12CT001 | 60LBA12CT001 | TT | SH FINISH OUTLET VENT-3 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ22CT004 | 60HAJ22CT004 | TYPE-K TC | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LBA12CT002 | 60LBA12CT002 | TT | SH FINISH OUTLET VENT-4 TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBA11CP001 | 60LBA11CP001 | PT | FINAL SH OUTLET PRESSURE - LEFT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 00 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA11CP002 | 60LBA11CP002 | PT | FINAL SH OUTLET PRESSURE - LEFT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 00 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA11CP003 | 60LBA11CP003 | PT | FINAL SH OUTLET PRESSURE - LEFT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 00 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA12CP001 | 60LBA12CP001 | PT | FINAL SH OUTLET PRESSURE - RIGHT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 00 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA12CP002 | 60LBA12CP002 | PT | FINAL SH OUTLET PRESSURE - RIGHT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 00 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60LBA12CP003 | 60LBA12CP003 | PT | FINAL SH OUTLET PRESSURE - RIGHT | STEAM | 1 | -- | 278 | 291.9 | kg/cm² | 603 | 608 | °C | -- | -- | -- | -- | -- | F/I,A,N | High Trip=301 | kg/cm² | 0 to 400 | kg/cm² | -- | -- | -- | -- | E | 00 | **TO BE OBTAINED FROM PIPING ENGG. | HART
60HAJ22CT005 | 60HAJ22CT005 | TYPE-K TC | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | 40 | 100 | -- | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | FLEXIBLE T/C = 30m
60LBA11CT003 | 60LBA11CT003 | TT | SH ERV LEFT-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAB91CT001 | 60LAB91CT001 | TYPE-K TC | FEED WATER LINE DRAIN | METAL | 1 | 33.4x6.35 |  |  | kg/cm² |  |  | °C | -- | -- | -- | -- | -- | -- | -- | -- |  | °C | -- | -- | -- | -- | P | 00
60LBA12CT003 | 60LBA12CT003 | TT | SH ERV RIGHT-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE21CT001 | 60LAE21CT001 | TYPE-K TC | RH / DSH "A" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 00
60LBA11CT004 | 60LBA11CT004 | TT | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE22CT001 | 60LAE22CT001 | TYPE-K TC | RH / DSH "B" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 00
60LBA12CT004 | 60LBA12CT004 | TT | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE71CT001 | 60LAE71CT001 | TYPE-K TC | SH / DSH STAGE-I "A" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00
60LBA11CT005 | 60LBA11CT005 | TT | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE72CT001 | 60LAE72CT001 | TYPE-K TC | SH / DSH STAGE-I "B" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 299.1 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00
60LBA12CT005 | 60LBA12CT005 | TT | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE91CT001 | 60LAE91CT001 | TYPE-K TC | SH / DSH STAGE-II "A" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00
60LBC11CT001 | 60LBC11CT001 | TT | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LAE92CT001 | 60LAE92CT001 | TYPE-K TC | SH / DSH STAGE-II "B" SPRAY WATER TEMP | WATER | 1 | 114.3x20 | 290.5 | 352.7 | kg/cm² | 308.9 | 348 | °C | -- | -- | -- | 10 | 100 | -- | -- | -- | 0 to 400 | °C | -- | -- | -- | -- | P | 00
60LBC11CT002 | 60LBC11CT002 | TT | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBA11CT001 | 60LBA11CT001 | TYPE-K TC | SH FINISH OUTLET VENT-1 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBC12CT001 | 60LBC12CT001 | TT | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBA11CT002 | 60LBA11CT002 | TYPE-K TC | SH FINISH OUTLET VENT-2 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBC12CT002 | 60LBC12CT002 | TT | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HAJ06CT001 to 006 | 60HAJ06CT001 to 006 | TYPE-K TC | LTRH INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- |  | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 500 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAJ07CT001 to 140 | 60HAJ07CT001 to 140 | TYPE-K TC | LTRH R-04 TUBE OUSIDE FLUE GAS METAL TEMP | METAL | 140 | -- | -- | -- | kg/cm² | -- | <614 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=614 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAJ07CT141 to 158 | 60HAJ07CT141 to 158 | TYPE-K TC | LTRH R-04 TUBE INSIDE FLUE GAS METAL TEMP | METAL | 18 | -- | -- | -- | kg/cm² | -- | <614 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAJ08CT001 to 006 | 60HAJ08CT001 to 006 | TYPE-K TC | LTRH OUTLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | <614 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60LAE20CP501 | 60LAE20CP501 | PI | RH SPRAY WATER PRESS | WATER | 1 | 114.3x13.49 | 156.182 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE20CP401 | 60LAE20CP401 | PP | RH SPRAY WATER PRESS | WATER | 1 | 114.3x13.49 | 156.182 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60LAE20CT501 | 60LAE20CT501 | TI | RH SPRAY WATER TEMP | WATER | 1 | 114.3x13.49 | 156.182 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | 10 | 100 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60LAE21CP501 | 60LAE21CP501 | PI | RH / DSH "A" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE21CP001 | 60LAE21CP001 | PT | RH / DSH "A" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60LBA11CT003 | 60LBA11CT003 | TYPE-K TC | SH ERV LEFT-VENT TEMP | METAL | 1 | 114.3 X 6.02 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LAE21CT001 | 60LAE21CT001 | TT | RH / DSH "A" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE21CF501 | 60LAE21CF501 | FE | RH / DSH "A" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60LAE21CF001 | 60LAE21CF001 | FT | RH / DSH "A" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE21CF002 | 60LAE21CF002 | FT | RH / DSH "A" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE22CP501 | 60LAE22CP501 | PI | RH / DSH 'B" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60LAE22CP001 | 60LAE22CP001 | PT | RH / DSH "B" SPRAY WATER PRESS | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 200 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60LBA11CT004 | 60LBA11CT004 | TYPE-K TC | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LAE22CT001 | 60LAE22CT001 | TT | RH / DSH "B" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 250 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LAE22CF501 | 60LAE22CF501 | FE | RH / DSH "B" SPRAY WATER | WATER | 1 | 88.9x11.13 | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60LAE22CF001 | 60LAE22CF001 | FT | RH / DSH "B" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LAE22CF002 | 60LAE22CF002 | FT | RH / DSH "B" SPRAY WATER | WATER | 1 | -- | 69 | 164 | kg/cm² | 191.4 | 197 | °C | 5 | 79.7 | t/hr | -- | -- | D/I,C | -- | -- | Later | mmWC | Later | t/hr | -- | -- | P | 00 |  | HART
60LBA11CT005 | 60LBA11CT005 | TYPE-K TC | SH LEFT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ21CT001 | 60HAJ21CT001 | TT | RH / DSH "A" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBA12CT001 | 60LBA12CT001 | TYPE-K TC | SH FINISH OUTLET VENT-3 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ21CT002 | 60HAJ21CT002 | TT | RH / DSH "A" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT401 | 60HAJ21CT401 | TW | RH / DSH "A" INLET TEMP | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60LBA12CT002 | 60LBA12CT002 | TYPE-K TC | SH FINISH OUTLET VENT-4 TEMP | METAL | 1 | 168.3 X 35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ22CT001 | 60HAJ22CT001 | TT | RH / DSH "B" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBA12CT003 | 60LBA12CT003 | TYPE-K TC | SH ERV RIGHT-VENT TEMP | METAL | 1 | 114.3 X 6.02 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ22CT002 | 60HAJ22CT002 | TT | RH / DSH "B" INLET | STEAM | 1 | -- | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ22CT401 | 60HAJ22CT401 | TW | RH / DSH "B" INLET TEMP | STEAM | 1 | 812.8x40 | 64.5 | 74 | kg/cm² | 545 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAJ21CP001 | 60HAJ21CP001 | PT | RH / DSH "A" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 100 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60LBA12CT004 | 60LBA12CT004 | TYPE-K TC | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ21CT003 | 60HAJ21CT003 | TT | RH / DSH "A" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBA12CT005 | 60LBA12CT005 | TYPE-K TC | SH RIGHT SPRING LOADED SAFETY VALVE-VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ21CT004 | 60HAJ21CT004 | TT | RH / DSH "A" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBB11CT001 | 60LBB11CT001 | TYPE-K TC | RH OUTLET LEFT- VENT TEMP | METAL | 1 | 76.2 X 5.08 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ21CT005 | 60HAJ21CT005 | TT | RH / DSH "A" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ21CT402 | 60HAJ21CT402 | TW | RH / DSH "A" OUTLET TEMP | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAJ22CP001 | 60HAJ22CP001 | PT | RH / DSH "B" OUTLET | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 100 | kg/cm² | -- | -- | -- | -- | P | 00 |  | PROFIBUS
60LBB11CT002 | 60LBB11CT002 | TYPE-K TC | RH ERV LEFT- VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ22CT003 | 60HAJ22CT003 | TT | RH / DSH "B" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBB11CT003 | 60LBB11CT003 | TYPE-K TC | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ22CT004 | 60HAJ22CT004 | TT | RH / DSH "B" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60LBB11CT004 | 60LBB11CT004 | TYPE-K TC | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60HAJ22CT005 | 60HAJ22CT005 | TT | RH / DSH "B" OUTLET | STEAM | 1 | -- | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | D/I,C | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | HART
60HAJ22CT402 | 60HAJ22CT402 | TW | RH / DSH "B" OUTLET TEMP | STEAM | 1 | 812.8x40 | 64.3 | 74 | kg/cm² | 542 | 560 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HAJ28CT001 to 006 | 60HAJ28CT001 to 006 | TYPE-K TC | RH FINISH INLET HEADER METAL TEMP | METAL | 6 | -- | -- | -- | kg/cm² | -- | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 750 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAJ29CT001 to 051 | 60HAJ29CT001 to 051 | TYPE-K TC | RH FINISH INLET TUBE OUTSIDE GAS PATH METAL TEMP | METAL | 51 | -- | -- | -- | kg/cm² | -- | 560 | °C | -- | -- | -- | -- | -- | D/I | -- | °C | 0 to 750 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAJ30CT001 to 090 | 60HAJ30CT001 to 090 | TYPE-K TC | RH FINISH OUTLET TUBE OUTSIDE GAS PATH METAL TEMP | METAL | 90 | -- | -- | -- | kg/cm² | -- | <636 | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=636 | °C | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAJ30CT091 to 103 | 60HAJ30CT091 to 103 | TYPE-K TC | RH FINISH OUTLET TUBE INSIDE GAS PATH METAL TEMP | METAL | 13 | -- | -- | -- | kg/cm² | -- | <636 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60HAJ31CT001 to 012 | 60HAJ31CT001 to 012 | TYPE-K TC | RH FINISH OUTLET HEADER METAL TEMP | METAL | 12 | -- | -- | -- | kg/cm² | -- | <636 | °C | -- | -- | -- | -- | -- | D/I | -- | -- | 0 to 800 | °C | -- | -- | -- | -- | T | 00 | PROFIBUS REMOTE I/O
60LBB12CT001 | 60LBB12CT001 | TYPE-K TC | RH OUTLET RIGHT- VENT TEMP | METAL | 1 | 76.2 X 5.08 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB11CT001 | 60LBB11CT001 | TT | RH OUTLET LEFT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT002 | 60LBB12CT002 | TYPE-K TC | RH ERV RIGHT- VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB11CT002 | 60LBB11CT002 | TT | RH ERV LEFT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT003 | 60LBB12CT003 | TYPE-K TC | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB11CT003 | 60LBB11CT003 | TT | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT004 | 60LBB12CT004 | TYPE-K TC | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB11CT004 | 60LBB11CT004 | TT | RH OUTLET LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBB12CT005 | 60LBB12CT005 | TYPE-K TC | RH ERV RIGHT- VENT TEMP | METAL | 1 | 219.1 X 8.18 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB12CT001 | 60LBB12CT001 | TT | RH OUTLET RIGHT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC11CT001 | 60LBC11CT001 | TYPE-K TC | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB12CT002 | 60LBB12CT002 | TT | RH ERV RIGHT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC11CT002 | 60LBC11CT002 | TYPE-K TC | RH INLET LEAD LEFT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB12CT005 | 60LBB12CT005 | TT | RH ERV RIGHT- VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC12CT001 | 60LBC12CT001 | TYPE-K TC | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB12CT003 | 60LBB12CT003 | TT | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 1 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LBC12CT002 | 60LBC12CT002 | TYPE-K TC | RH INLET LEAD RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | 273 X 6.35 | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 200 | °C | -- | -- | -- | -- | P | 00
60LBB12CT004 | 60LBB12CT004 | TT | RH OUTLET RIGHT- SPRING LOADED SAFETY VALVE 2 VENT TEMP | METAL | 1 | -- | -- | -- | kg/cm² | 50 to 75 | -- | °C | -- | -- | -- | -- | -- | D/I,A | High Alarm=75 | °C | 0 to 200 | °C | -- | -- | -- | -- | P | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB01CT501 | 60HCB01CT501 | TI | SB RH STM TEMP (BEFORE PRV) | STEAM | 1 | 114.3x6.02 | 64.6 | 75 | kg/cm² | 374 | 400 | °C | -- | -- | -- | 30 | 140 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 01
60HCB01CP401 | 60HCB01CP401 | PP | SB RH STM PRESS (BEFORE PRV) | STEAM | 1 | 114.3x6.02 | 64.6 | 75 | kg/cm² | 374 | 400 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HCB01CP501 | 60HCB01CP501 | PI | SB RH STM PRESS (BEFORE PRV) | STEAM | 1 | 114.3x6.02 | 64.6 | 75 | kg/cm² | 374 | 400 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB03CT501 | 60HCB03CT501 | TI | SB SH STM TEMP (BEFORE PRV) | STEAM | 1 | 127x20 | 295.8 | 308.7 | kg/cm² | 516 | 537 | °C | -- | -- | -- | 21.28 | 220 | L/I | -- | -- |  | °C | -- | -- | -- | -- | T | 00
60HCB03CP401 | 60HCB03CP401 | PP | SB SH STM PRESS (BEFORE PRV) | STEAM | 1 | 127x20 | 295.8 | 308.7 | kg/cm² | 516 | 537 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HCB03CP501 | 60HCB03CP501 | PI | SB SH STM PRESS (BEFORE PRV) | STEAM | 1 | 127x20 | 295.8 | 308.7 | kg/cm² | 516 | 537 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB01CP001 | 60HCB01CP001 | PT | SB STM PRESS (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Low=18.4 | kg/cm² | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 00 |  | PROFIBUS
60HCB01CP002 | 60HCB01CP002 | PT | SB STM PRESS (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Low=18.4 | kg/cm² | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 00 |  | PROFIBUS
60HCB01CP502 | 60HCB01CP502 | PI | SB STM PRESS (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB01CT001 | 60HCB01CT001 | TYPE-K TC | SB STM TEMP (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 58 | 220 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB01CT001 | 60HCB01CT001 | TT | SB STM TEMP (AFTER PRV) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,A | Low Alarm= 290 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB01CT401 | 60HCB01CT401 | TW | SB STM TEMP (AFTER PRV) | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | T | -- | -- | -- | -- | -- | -- | -- | -- | -- | 00
60HCB01CF501 | 60HCB01CF501 | FE | SOOTBLOWER STM FLOW | STEAM | 1 | 127x12.5 | 40 | 50 | kg/cm² | 380 | 500 | °C | 22 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60HCB01CF001 | 60HCB01CF001 | FIT | SOOTBLOWER STM FLOW | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 22 | -- | t/hr | -- | -- | SB/I | -- | -- | Later | mmWC | 0-28 | t/hr | -- | -- | E | 00 |  | PROFIBUS
60HCB13CP501 | 60HCB13CP501 | PI | SB STM PRESS (LRSB LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB13CF501 | 60HCB13CF501 | FE | SOOTBLOWER STM FLOW (LRSB LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60HCB13CF001 | 60HCB13CF001 | FIT | SOOTBLOWER STM FLOW (LRSB LINE-RIGHT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | SB/I,N | Low=2.37 | t/hr | Later | mmWC | 0-9 | t/hr | -- | -- | E | 00 |  | PROFIBUS
60HCB13CT001 | 60HCB13CT001 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB13CT001 | 60HCB13CT001 | TT | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB13CT002 | 60HCB13CT002 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB13CT002 | 60HCB13CT002 | TT | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB13CT003 | 60HCB13CT003 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB13CT003 | 60HCB13CT003 | TT | SB CNDS TEMP (LRSB DRAIN LINE-RIGHT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB14CP501 | 60HCB14CP501 | PI | SB STM PRESS (LRSB LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB14CF501 | 60HCB14CF501 | FE | SOOTBLOWER STM FLOW (LRSB LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60HCB14CF001 | 60HCB14CF001 | FIT | SOOTBLOWER STM FLOW (LRSB LINE-LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 4.56 | -- | t/hr | -- | -- | SB/I,N | Low=2.37 | t/hr | Later | mmWC | 0-9 | t/hr | -- | -- | E | 00 |  | PROFIBUS
60HCB14CT001 | 60HCB14CT001 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB14CT001 | 60HCB14CT001 | TT | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB14CT002 | 60HCB14CT002 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB14CT002 | 60HCB14CT002 | TT | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB14CT003 | 60HCB14CT003 | TYPE-K TC | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB14CT003 | 60HCB14CT003 | TT | SB CNDS TEMP (LRSB DRAIN LINE-LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB06CP501 | 60HCB06CP501 | PI | APH "A" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB06CP001 | 60HCB06CP001 | PT | APH "A" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 00 |  | PROFIBUS
60HCB05CP501 | 60HCB05CP501 | PI | APH "A" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB05CP001 | 60HCB05CP001 | PT | APH "A" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 00 |  | PROFIBUS
60HCB07CT001 | 60HCB07CT001 | TYPE-K TC | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB07CT001 | 60HCB07CT001 | TT | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB07CT002 | 60HCB07CT002 | TYPE-K TC | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB07CT002 | 60HCB07CT002 | TT | SB CNDS TEMP (APH "A"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB07CT003 | 60HCB07CT003 | TYPE-K TC | SB CNDS TEMP (APH "A"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB07CT003 | 60HCB07CT003 | TT | SB CNDS TEMP (APH "A"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB09CP501 | 60HCB09CP501 | PI | APH "B" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB09CP001 | 60HCB09CP001 | PT | APH "B" SOOTBLOWER STEAM PRESS (COLD END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 00 |  | PROFIBUS
60HCB08CP501 | 60HCB08CP501 | PI | APH "B" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB08CP001 | 60HCB08CP001 | PT | APH "B" SOOTBLOWER STEAM PRESS (HOT END) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 75 | kg/cm² | -- | -- | -- | -- | E | 00 |  | PROFIBUS
60HCB10CT001 | 60HCB10CT001 | TYPE-K TC | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB10CT001 | 60HCB10CT001 | TT | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB10CT002 | 60HCB10CT002 | TYPE-K TC | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB10CT002 | 60HCB10CT002 | TT | SB CNDS TEMP (APH "B"SB DRAIN LINE) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB10CT003 | 60HCB10CT003 | TYPE-K TC | SB CNDS TEMP (APH "B"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB10CT003 | 60HCB10CT003 | TT | SB CNDS TEMP (APH "B"SB DRAIN LINE) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB11CP501 | 60HCB11CP501 | PI | SB STM PRESS (WB LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB11CF501 | 60HCB11CF501 | FE | SOOTBLOWER STM FLOW (WB LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60HCB11CF001 | 60HCB11CF001 | FIT | SOOTBLOWER STM FLOW (WB LINE-FRONT & LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | SB/I,N | Low=1.8 | t/hr | Later | mmWC | 0-4 | t/hr | -- | -- | E | 00 |  | PROFIBUS
60HCB11CT001 | 60HCB11CT001 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB11CT001 | 60HCB11CT001 | TT | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB11CT002 | 60HCB11CT002 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB11CT002 | 60HCB11CT002 | TT | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB11CT003 | 60HCB11CT003 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB11CT003 | 60HCB11CT003 | TT | SB CNDS TEMP (WB DRAIN LINE-FRONT & LEFT) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB12CP501 | 60HCB12CP501 | PI | SB STM PRESS (WB LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | L/I | -- | -- |  | kg/cm² | -- | -- | -- | 1/2" NPT(M) | T | 01
60HCB12CF501 | 60HCB12CF501 | FE | SOOTBLOWER STM FLOW (WB LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | T | 00
60HCB12CF001 | 60HCB12CF001 | FIT | SOOTBLOWER STM FLOW (WB LINE-RIGHT & REAR) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | 2.67 | -- | t/hr | -- | -- | SB/I,N | Low=1.8 | t/hr | Later | mmWC | 0-4 | t/hr | -- | -- | E | 00 |  | PROFIBUS
60HCB12CT001 | 60HCB12CT001 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB12CT001 | 60HCB12CT001 | TT | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB12CT002 | 60HCB12CT002 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | 88.9x5.49 | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | 50 | 120 | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB12CT002 | 60HCB12CT002 | TT | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | STEAM | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I,C,N | Close = >250, Open = <240 | °C | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60HCB12CT003 | 60HCB12CT003 | TYPE-K TC | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | -- | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00
60HCB12CT003 | 60HCB12CT003 | TT | SB CNDS TEMP (WB DRAIN LINE-RIGHT & REAR) | METAL | 1 | -- | 40 | 50 | kg/cm² | 380 | 500 | °C | -- | -- | -- | -- | -- | SB/I | -- | -- | 0 to 600 | °C | -- | -- | -- | -- | E | 00 | SINGLE INPUT DIN RAIL MOUNTED TT IN JB | PROFIBUS
60LDN01CP502 | 60LDN01CP502 | PI | DISTRIBUTION LINE PRESSURE | NITROGEN | 1 | 60.3x5.54 | 5 | -- | kg/cm² | Ambient | -- | °C | -- | -- | -- | -- | -- | L/I | -- | -- | -- | -- | -- | -- | -- | 1/2" NPT(M) | V | 01
60LDN01CP501 | 60LDN01CP501 | PI | PRESSURE AT SUPPLY MANIFOLD | NITROGEN | 1 | 60.3x5.54 | 5 | -- | kg/cm² | Ambient | -- | °C | -- | -- | -- | -- | -- | L/I | -- | -- | -- | -- | -- | -- | -- | 1/2" NPT(M) | V | 01
Note on R1: Same as Lara, as confirmed by L&I over phone on 17.07.25
Note on A3: 10LAB91CT001 to be retained in P&ID instead of 10LAB51CT012
Note on B3: 10LAB91CT001 to be retained in P&ID instead of 10LAB51CT012
Note on T23: C PT -1733 yet to update
Note on T25: C PT -1733 yet to update
Note on H38: As per Talcher
Note on K38: As per Talcher
Note on H39: As per Talcher
Note on K39: As per Talcher
Note on H40: As per Talcher
Note on K40: As per Talcher
Note on R105: As per Teletalk with Mr Nil on 16.10.24
Note on R107: As per Teletalk with Mr Nil on 16.10.24
Note on R117: As per Teletalk with Mr Nil on 16.10.24
Note on R119: As per Teletalk with Mr Nil on 16.10.24
Note on R129: As per Teletalk with Mr Nil on 16.10.24
Note on R131: As per Teletalk with Mr Nil on 16.10.24
Note on R141: As per Teletalk with Mr Nil on 16.10.24
Note on R143: As per Teletalk with Mr Nil on 16.10.24
Note on H275: In R0 of Lara 334.5-0.05
Note on H276: In R0 of Lara 334.5-0.05
Note on H277: In R0 of Lara 334.5-0.05
Note on H278: In R0 of Lara 306.12
Note on H279: In R0 of Lara 306.12
Note on H281: In R0 of Lara 306.12
Note on H282: In R0 of Lara 306.12
Note on H283: In R0 of Lara 306.12
Note on H284: In R0 of Lara 306.12
Note on H285: In R0 of Lara 306.12
Note on H286: In R0 of Lara 306.12
Note on H288: In R0 of Lara 306.12
Note on H289: In R0 of Lara 306.12
Note on H290: In R0 of Lara 306.12
Note on H291: In R0 of Lara 306.12
Note on H322: In R0 of Lara 334.5-0.3
Note on H323: In R0 of Lara 334.5-0.3
Note on H324: In R0 of Lara 334.5-0.3
Note on H325: In R0 of Lara 289.81
Note on H326: In R0 of Lara 289.81
Note on H328: In R0 of Lara 289.81
Note on H329: In R0 of Lara 289.81
Note on H330: In R0 of Lara 289.81
Note on H331: In R0 of Lara 289.81
Note on H332: In R0 of Lara 289.81
Note on H333: In R0 of Lara 289.81
Note on H335: In R0 of Lara 289.81
Note on H336: In R0 of Lara 289.81
Note on H337: In R0 of Lara 289.81
Note on H338: In R0 of Lara 289.81
Note on A397: 10LAB91CT001 to be retained in P&ID instead of 10LAB51CT012
Note on B397: 10LAB91CT001 to be retained in P&ID instead of 10LAB51CT012
Note on H403: In R0 of Lara 306.12
Note on H405: In R0 of Lara 306.12
Note on H407: In R0 of Lara 289.81
Note on H409: In R0 of Lara 289.81
Note on N426: 5 in Lara CPT, 4 in Sipat PID, 4.5 in Singrauli CPT
Note on N427: 5 in Lara CPT, 4 in Sipat PID, 4.5 in Singrauli CPT
Note on N428: 5 in Lara CPT, 4 in Sipat PID, 4.5 in Singrauli CPT
Note on N433: 5 in Lara CPT, 4 in Sipat PID, 4.5 in Singrauli CPT
Note on N434: 5 in Lara CPT, 4 in Sipat PID, 4.5 in Singrauli CPT
Note on N435: 5 in Lara CPT, 4 in Sipat PID, 4.5 in Singrauli CPT
Note on R485: As confirmed by Mr Nil Mohan Sir over phone on 29.07.25
Note on A555: 00LDN01CP502 as per P&ID
Note on B555: 00LDN01CP502 as per P&ID
Note on A556: LDN01CP501 as per P&ID
Note on B556: LDN01CP501 as per P&ID